## system_meta
model_config_param | value | notes
MODEL_NAME | Coal-fired 600W power station
INFRASTRUCTURE_LEVEL | facility
SYSTEM_CLASS | PowerStation
SYSTEM_SUBCLASS | Thermal Power Station
SYSTEM_COMPONENT_LOCATION_CONF | undefined
RESTORATION_TIME_UNIT | days
HAZARD_INTENSITY_MEASURE_PARAM | PGA
HAZARD_INTENSITY_MEASURE_UNIT | g

## table_description
table | description | note
component_list | This file lists the instances of various component types within the system. Component design level x.xx g. | Cost fractions define economic value of the individual component relative to the cost of entire system. Data includes a 3% allowance for components not included in the model.
component_connections | Network connections. Each pair of nodes implies a connecting edge. Directionality is defined by order of nodes in a row (Orig -> Dest). | Used by: (1) network algorithm package for flow calculations, (2) Pygraphviz to draw the system layout.
supply_setup | Necessary input materiél required for plant operation | Capacity given as percentage
output_setup | Treatment Capacity in Mega Litres per Day (MLD)
comp_type_dmg_algo | List of component types with fragility and recovery data | Fragilities are defined according to discrete damage states. Recovery time is in WEEKS. The suffix SDL refers to component Seismic Design Level. [SDL1: 0.2g PGA, SDL2: 0.35g PGA, SDL3: 0.4g PGA]
damage_state_def |  | Definitions of damage states of the list of component types in the system

## component_list
component_id | component_type | component_class | cost_fraction | node_type | node_cluster | operating_capacity | pos_x | pos_y | site_id
coal_supply | SYSTEM_INPUT | Coal Delivery and Storage | 0 | supply | INPUT | 1
unloader_1 | Unloader | Coal Delivery and Storage | 0.025954 | transshipment | Fuel Supply | 1
unloader_2 | Unloader | Coal Delivery and Storage | 0.025954 | transshipment | Fuel Supply | 1
coal_yard | Coal Yard | Coal Delivery and Storage | 0.01 | transshipment | Fuel Storage | 1
stacker_reclaimer_1 | Stacker Reclaimer | Stackers | 0.019923 | transshipment | Stackers | 1
stacker_reclaimer_2 | Stacker Reclaimer | Stackers | 0.019923 | transshipment | Stackers | 1
stacker_reclaimer_3 | Stacker Reclaimer | Stackers | 0.019923 | transshipment | Stackers | 1
supply_conv_1 | Supply Conveyor | Supply Conveyors | 0.0033205 | transshipment | Supply Conveyors | 1
supply_conv_2 | Supply Conveyor | Supply Conveyors | 0.0033205 | transshipment | Supply Conveyors | 1
supply_conv_3 | Supply Conveyor | Supply Conveyors | 0.0033205 | transshipment | Supply Conveyors | 1
supply_conv_4 | Supply Conveyor | Supply Conveyors | 0.0033205 | transshipment | Supply Conveyors | 1
feed_conv_1 | Main Feed Conveyor | Feed Conveyors | 0.0066411 | transshipment | Feed Conveyors | 1
feed_conv_2 | Main Feed Conveyor | Feed Conveyors | 0.0066411 | transshipment | Feed Conveyors | 1
water_supply | Fresh Water Supply | Boiler System | 0.02319 | supply | Boiler System | 1
demin_plant | Demineralisation Plant | Boiler System | 0.0086513 | transshipment | Boiler System | 1
boiler_1 | Boiler | Boiler System | 0.14429 | transshipment | Boiler System | 1
boiler_2 | Boiler | Boiler System | 0.14429 | transshipment | Boiler System | 1
precip_1a | Electrostatic Precipitator | Electrostatic Precipitators | 0.0013359 | transshipment | Electrostatic Precipitators | 1
precip_1b | Electrostatic Precipitator | Electrostatic Precipitators | 0.0013359 | transshipment | Electrostatic Precipitators | 1
precip_2a | Electrostatic Precipitator | Electrostatic Precipitators | 0.0013359 | transshipment | Electrostatic Precipitators | 1
precip_2b | Electrostatic Precipitator | Electrostatic Precipitators | 0.0013359 | transshipment | Electrostatic Precipitators | 1
ash_disposal | Ash Disposal System | Emission Management | 0.005 | dependency | Emission Management | 1
stack_1 | Stack | Emission Management | 0.0066793 | transshipment | Emission Management | 1
stack_2 | Stack | Emission Management | 0.0066793 | transshipment | Emission Management | 1
pwr_house | Power House | Generator Plant Subsystem | 0.1 | dependency | none | 1
turbine_condenser_1 | Turbine and Condenser | Condenser | 0.12429 | transshipment | Condenser | 1
turbine_condenser_2 | Turbine and Condenser | Condenser | 0.12429 | transshipment | Condenser | 1
gen_1 | Generator | Generator Plant Subsystem | 0.046543 | transshipment | Generator Plant Subsystem | 1
gen_2 | Generator | Generator Plant Subsystem | 0.046543 | transshipment | Generator Plant Subsystem | 1
tr_1 | Stepup Transformer | Stepup Transformer | 0.012977 | transshipment | Stepup Transformer | 1
tr_2 | Stepup Transformer | Stepup Transformer | 0.012977 | transshipment | Stepup Transformer | 1
output_1 | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | OUTPUT | 1
output_2 | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | OUTPUT | 1

## component_connections
origin | destination | link_capacity | weight
coal_supply | unloader_1 | 1 | 1
coal_supply | unloader_2 | 1 | 1
unloader_1 | coal_yard | 1 | 1
unloader_2 | coal_yard | 1 | 1
coal_yard | stacker_reclaimer_1 | 1 | 1
coal_yard | stacker_reclaimer_2 | 1 | 1
coal_yard | stacker_reclaimer_3 | 1 | 1
stacker_reclaimer_1 | supply_conv_1 | 1 | 1
stacker_reclaimer_2 | supply_conv_2 | 1 | 1
stacker_reclaimer_3 | supply_conv_3 | 1 | 1
supply_conv_1 | feed_conv_1 | 1 | 1
supply_conv_2 | feed_conv_1 | 1 | 1
supply_conv_3 | feed_conv_2 | 1 | 1
supply_conv_1 | supply_conv_4 | 1 | 1
supply_conv_4 | supply_conv_3 | 1 | 1
supply_conv_3 | supply_conv_4 | 1 | 1
feed_conv_1 | boiler_1 | 1 | 1
feed_conv_2 | boiler_2 | 1 | 1
feed_conv_1 | feed_conv_2 | 1 | 1
demin_plant | boiler_1 | 1 | 1
demin_plant | boiler_2 | 1 | 1
water_supply | demin_plant | 1 | 1
boiler_1 | precip_1a | 1 | 1
boiler_1 | precip_1b | 1 | 1
boiler_2 | precip_2a | 1 | 1
boiler_2 | precip_2b | 1 | 1
precip_1a | stack_1 | 1 | 1
precip_1b | stack_1 | 1 | 1
precip_2a | stack_2 | 1 | 1
precip_2b | stack_2 | 1 | 1
ash_disposal | stack_1 | 1 | 1
ash_disposal | stack_2 | 1 | 1
stack_1 | turbine_condenser_1 | 1 | 1
stack_2 | turbine_condenser_2 | 1 | 1
turbine_condenser_1 | gen_1 | 1 | 1
turbine_condenser_2 | gen_2 | 1 | 1
gen_1 | tr_1 | 1 | 1
gen_2 | tr_2 | 1 | 1
pwr_house | gen_1 | 1 | 1
pwr_house | gen_2 | 1 | 1
tr_1 | output_1 | 1 | 1
tr_2 | output_2 | 1 | 1

## supply_setup
input_node | input_capacity | capacity_fraction | commodity_type
coal_supply | 100 | 1 | coal
water_supply | 100 | 1 | water

## output_setup
output_node | production_node | output_node_capacity | capacity_fraction | priority
output_1 | gen_1 | 300 | 0.5 | 2
output_2 | gen_2 | 300 | 0.5 | 1

## comp_type_dmg_algo
id | component_type | damage_state | is_piecewise | damage_function | median | beta | location | damage_ratio | functionality | minimum | upper_limit | lower_limit | recovery_function | recovery_param1 | recovery_param2 | recovery_95percentile | data_source
1 | Ash Disposal System | DS1 Slight | no | Lognormal | 0.45 | 0 | 0.2 | 0.05 | 1 | NA | null | null | Normal | 0.2 | 0.060796 | 0.1 | SIM to supply conveyor
2 | Ash Disposal System | DS2 Moderate | no | Lognormal | 0.59 | 0 | 0.3 | 0.3 | 0 | NA | null | null | Normal | 0.5 | 0.060796 | 0.1 | SIM to supply conveyor
3 | Ash Disposal System | DS3 Extensive | no | Lognormal | 0.775 | 0 | 0.35 | 0.75 | 0 | NA | null | null | Normal | 1 | 0.30398 | 0.5 | SIM to supply conveyor
4 | Ash Disposal System | DS4 Complete | no | Lognormal | 1 | 0 | 0.35 | 1 | 0 | NA | null | null | Normal | 4.3 | 0.60796 | 1 | SIM to supply conveyor
5 | Boiler | DS1 Slight | no | Lognormal | 0.46 | 0 | 0.23 | 0.1 | 1 | NA | null | null | Normal | 3 | 0.60796 | 1 | Not Available.
6 | Boiler | DS2 Moderate | no | Lognormal | 0.57 | 0 | 0.25 | 0.3 | 0 | NA | null | null | Normal | 20 | 1.2159 | 2 | Not Available.
7 | Boiler | DS3 Extensive | no | Lognormal | 0.825 | 0 | 0.35 | 0.9 | 0 | NA | null | null | Normal | 60 | 2.4318 | 4 | Not Available.
8 | Boiler | DS4 Complete | no | Lognormal | 1.8 | 0 | 0.6 | 1.3 | 0 | NA | null | null | Normal | 102.8571 | 4.8637 | 8 | Not Available.
9 | Coal Yard | DS1 Slight | no | Lognormal | 0.67 | 0 | 0.2 | 0.06 | 1 | NA | null | null | Normal | 0.2 | 0.060796 | 0.1 | Not Available.
10 | Coal Yard | DS2 Moderate | no | Lognormal | 0.85 | 0 | 0.27 | 0.3 | 1 | NA | null | null | Normal | 0.5 | 0.060796 | 0.1 | Not Available.
11 | Coal Yard | DS3 Extensive | no | Lognormal | 1.05 | 0 | 0.35 | 0.75 | 0 | NA | null | null | Normal | 1 | 0.30398 | 0.5 | Not Available.
12 | Coal Yard | DS4 Complete | no | Lognormal | 1.35 | 0 | 0.35 | 1 | 0 | NA | null | null | Normal | 4.3 | 0.60796 | 1 | Not Available.
13 | Cooling System | DS1 Slight | no | Lognormal | 0.42 | 0 | 0.375 | 0.1 | 1 | NA | null | null | Normal | 1 | 0.30398 | 0.5 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
14 | Cooling System | DS2 Moderate | no | Lognormal | 0.57 | 0 | 0.375 | 0.3 | 0 | NA | null | null | Normal | 3 | 0.60796 | 1 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
15 | Cooling System | DS3 Extensive | no | Lognormal | 0.78 | 0 | 0.475 | 0.75 | 0 | NA | null | null | Normal | 15 | 1.8239 | 3 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
16 | Cooling System | DS4 Complete | no | Lognormal | 1.33 | 0 | 0.475 | 1 | 0 | NA | null | null | Normal | 30 | 2.4318 | 4 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
17 | Demineralisation Plant | DS1 Slight | no | Lognormal | 0.42 | 0 | 0.16 | 0.1 | 1 | NA | null | null | Normal | 5 | 0.18239 | 0.3 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
18 | Demineralisation Plant | DS2 Moderate | no | Lognormal | 0.57 | 0 | 0.28 | 0.3 | 0 | NA | null | null | Normal | 10 | 1.2159 | 2 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
19 | Demineralisation Plant | DS3 Extensive | no | Lognormal | 0.78 | 0 | 0.35 | 0.75 | 0 | NA | null | null | Normal | 21 | 1.8239 | 3 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
20 | Demineralisation Plant | DS4 Complete | no | Lognormal | 1.33 | 0 | 0.4 | 1 | 0 | NA | null | null | Normal | 42.8571 | 2.4318 | 4 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
21 | Electrostatic Precipitator | DS1 Slight | no | Lognormal | 0.35 | 0 | 0.4 | 0.1 | 0 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | HAZUS-MH Table D8.8 Electircal equipment
22 | Electrostatic Precipitator | DS2 Moderate | no | Lognormal | 0.55 | 0 | 0.5 | 0.3 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | HAZUS-MH Table D8.8 Electircal equipment
23 | Electrostatic Precipitator | DS3 Extensive | no | Lognormal | 0.75 | 0 | 0.4 | 0.75 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Sim to main feed conveyor
24 | Electrostatic Precipitator | DS4 Complete | no | Lognormal | 1 | 0 | 0.4 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Sim to main feed conveyor
25 | Fresh Water Supply | DS1 Slight | no | Lognormal | 0.43 | 0 | 0.16 | 0.1 | 1 | NA | null | null | Normal | 1 | 0.12159 | 0.2 | HAZUS-MH MR3 Table 8.6 Small Pumping Plants
26 | Fresh Water Supply | DS2 Moderate | no | Lognormal | 0.57 | 0 | 0.27 | 0.3 | 0 | NA | null | null | Normal | 4 | 0.30398 | 0.5 | Not Available.
27 | Fresh Water Supply | DS3 Extensive | no | Lognormal | 0.78 | 0 | 0.35 | 0.75 | 0 | NA | null | null | Normal | 8 | 0.91194 | 1.5 | Not Available.
28 | Fresh Water Supply | DS4 Complete | no | Lognormal | 1.33 | 0 | 0.4 | 1 | 0 | NA | null | null | Normal | 12 | 1.8239 | 3 | Not Available.
29 | Generator | DS1 Slight | no | Lognormal | 0.75 | 0 | 0.28 | 0.03 | 0 | NA | null | null | Normal | 3 | 0.60796 | 1 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
30 | Generator | DS2 Moderate | no | Lognormal | 1 | 0 | 0.3 | 0.15 | 0 | NA | null | null | Normal | 20 | 1.2159 | 2 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
31 | Generator | DS3 Extensive | no | Lognormal | 1.33 | 0 | 0.34 | 0.4 | 0 | NA | null | null | Normal | 60 | 2.4318 | 4 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
32 | Generator | DS4 Complete | no | Lognormal | 1.55 | 0 | 0.28 | 1.2 | 0 | NA | null | null | Normal | 102.8571 | 4.8637 | 8 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
33 | Main Feed Conveyor | DS1 Slight | no | Lognormal | 0.45 | 0 | 0.2 | 0.06 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Not Available.
34 | Main Feed Conveyor | DS2 Moderate | no | Lognormal | 0.585 | 0 | 0.295 | 0.3 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | Not Available.
35 | Main Feed Conveyor | DS3 Extensive | no | Lognormal | 0.75 | 0 | 0.35 | 0.75 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
36 | Main Feed Conveyor | DS4 Complete | no | Lognormal | 1 | 0 | 0.35 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
37 | Power House | DS1 Slight | no | Lognormal | 0.475 | 0 | 0.25 | 0.06 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Not Available.
38 | Power House | DS2 Moderate | no | Lognormal | 0.615 | 0 | 0.33 | 0.3 | 1 | NA | null | null | Normal | 17 | 0.60796 | 1 | Not Available.
39 | Power House | DS3 Extensive | no | Lognormal | 0.77 | 0 | 0.4 | 0.75 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
40 | Power House | DS4 Complete | no | Lognormal | 1 | 0 | 0.4 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
41 | Stack | DS1 Slight | no | Lognormal | 0.67 | 0 | 0.2 | 0.1 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Not Available.
42 | Stack | DS2 Moderate | no | Lognormal | 0.85 | 0 | 0.27 | 0.4 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | Not Available.
43 | Stack | DS3 Extensive | no | Lognormal | 1.05 | 0 | 0.35 | 0.8 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
44 | Stack | DS4 Complete | no | Lognormal | 1.35 | 0 | 0.35 | 1.2 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
45 | Stacker Reclaimer | DS1 Slight | no | Lognormal | 0.39 | 0 | 0.55 | 0.06 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
46 | Stacker Reclaimer | DS2 Moderate | no | Lognormal | 0.595 | 0 | 0.61 | 0.2 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
47 | Stacker Reclaimer | DS3 Extensive | no | Lognormal | 0.795 | 0 | 0.595 | 0.8 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
48 | Stacker Reclaimer | DS4 Complete | no | Lognormal | 1 | 0 | 0.505 | 1.2 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
49 | Stepup Transformer | DS1 Slight | no | Lognormal | 0.55 | 0 | 0.34 | 0.03 | 0 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
50 | Stepup Transformer | DS2 Moderate | no | Lognormal | 0.9 | 0 | 0.26 | 0.1 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
51 | Stepup Transformer | DS3 Extensive | no | Lognormal | 1.25 | 0 | 0.21 | 0.15 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
52 | Stepup Transformer | DS4 Complete | no | Lognormal | 1.65 | 0 | 0.11 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
53 | Supply Conveyor | DS1 Slight | no | Lognormal | 0.335 | 0 | 0.275 | 0.1 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Not Available.
54 | Supply Conveyor | DS2 Moderate | no | Lognormal | 0.5 | 0 | 0.34 | 0.4 | 1 | NA | null | null | Normal | 17 | 0.60796 | 1 | Not Available.
55 | Supply Conveyor | DS3 Extensive | no | Lognormal | 0.75 | 0 | 0.435 | 0.8 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
56 | Supply Conveyor | DS4 Complete | no | Lognormal | 1 | 0 | 0.455 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
57 | Turbine and Condenser | DS1 Slight | no | Lognormal | 0.75 | 0 | 0.28 | 0.1 | 0 | NA | null | null | Normal | 5 | 0.60796 | 1 | Not Available.
58 | Turbine and Condenser | DS2 Moderate | no | Lognormal | 1 | 0 | 0.3 | 0.3 | 0 | NA | null | null | Normal | 20 | 1.2159 | 2 | Not Available.
59 | Turbine and Condenser | DS3 Extensive | no | Lognormal | 1.33 | 0 | 0.34 | 0.85 | 0 | NA | null | null | Normal | 50 | 2.4318 | 4 | Not Available.
60 | Turbine and Condenser | DS4 Complete | no | Lognormal | 1.55 | 0 | 0.28 | 1.2 | 0 | NA | null | null | Normal | 102.8571 | 4.8637 | 8 | Not Available.
61 | Unloader | DS1 Slight | no | Lognormal | 0.44 | 0 | 0.55 | 0.06 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
62 | Unloader | DS2 Moderate | no | Lognormal | 0.645 | 0 | 0.61 | 0.2 | 0.6 | NA | null | null | Normal | 17 | 0.60796 | 1 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
63 | Unloader | DS3 Extensive | no | Lognormal | 0.845 | 0 | 0.595 | 0.8 | 0.2 | NA | null | null | Normal | 37 | 1.2159 | 2 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
64 | Unloader | DS4 Complete | no | Lognormal | 1.05 | 0 | 0.505 | 1.2 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
65 | Ash Disposal System SDL1 | DS1 Slight | no | Lognormal | 0.28 | 0 | 0.25 | 0.05 | 1 | NA | null | null | Normal | 0.2 | 0.060796 | 0.1 | Similar to main feed conveyor but with increased variability.
66 | Ash Disposal System SDL1 | DS2 Moderate | no | Lognormal | 0.43 | 0 | 0.35 | 0.3 | 0 | NA | null | null | Normal | 0.5 | 0.060796 | 0.1 | Not Available.
67 | Ash Disposal System SDL1 | DS3 Extensive | no | Lognormal | 0.6 | 0 | 0.4 | 0.75 | 0 | NA | null | null | Normal | 1 | 0.30398 | 0.5 | Not Available.
68 | Ash Disposal System SDL1 | DS4 Complete | no | Lognormal | 0.85 | 0 | 0.4 | 1 | 0 | NA | null | null | Normal | 4.3 | 0.60796 | 1 | Not Available.
69 | Boiler SDL1 | DS1 Slight | no | Lognormal | 0.28 | 0 | 0.26 | 0.1 | 1 | NA | null | null | Normal | 3 | 0.60796 | 1 | Using MH Hazus Table D8.8 for Boilers and pressure vessels anchored assuming HAZUS equivalent to 0.3g design level.
70 | Boiler SDL1 | DS2 Moderate | no | Lognormal | 0.42 | 0 | 0.31 | 0.3 | 0 | NA | null | null | Normal | 20 | 1.2159 | 2 | Not Available.
71 | Boiler SDL1 | DS3 Extensive | no | Lognormal | 0.67 | 0 | 0.35 | 0.9 | 0 | NA | null | null | Normal | 60 | 2.4318 | 4 | Not Available.
72 | Boiler SDL1 | DS4 Complete | no | Lognormal | 1.7 | 0 | 0.6 | 1.3 | 0 | NA | null | null | Normal | 102.8571 | 4.8637 | 8 | Not Available.
73 | Coal Yard SDL1 | DS1 Slight | no | Lognormal | 0.67 | 0 | 0.2 | 0.06 | 1 | NA | null | null | Normal | 0.2 | 0.060796 | 0.1 | Wind dominance to effective desing resistance of 0.6g
74 | Coal Yard SDL1 | DS2 Moderate | no | Lognormal | 0.85 | 0 | 0.27 | 0.3 | 1 | NA | null | null | Normal | 0.5 | 0.060796 | 0.1 | Not Available.
75 | Coal Yard SDL1 | DS3 Extensive | no | Lognormal | 1.05 | 0 | 0.35 | 0.75 | 0 | NA | null | null | Normal | 1 | 0.30398 | 0.5 | Not Available.
76 | Coal Yard SDL1 | DS4 Complete | no | Lognormal | 1.35 | 0 | 0.35 | 1 | 0 | NA | null | null | Normal | 4.3 | 0.60796 | 1 | Not Available.
77 | Cooling System SDL1 | DS1 Slight | no | Lognormal | 0.27 | 0 | 0.45 | 0.1 | 1 | NA | null | null | Normal | 1 | 0.30398 | 0.5 | Assume damage functions for medium water treatment plants MH HAZUS Table 8.3 corresponds with 0.3g design
78 | Cooling System SDL1 | DS2 Moderate | no | Lognormal | 0.42 | 0 | 0.45 | 0.3 | 0 | NA | null | null | Normal | 3 | 0.60796 | 1 | Not Available.
79 | Cooling System SDL1 | DS3 Extensive | no | Lognormal | 0.63 | 0 | 0.55 | 0.75 | 0 | NA | null | null | Normal | 15 | 1.8239 | 3 | Not Available.
80 | Cooling System SDL1 | DS4 Complete | no | Lognormal | 1.18 | 0 | 0.55 | 1 | 0 | NA | null | null | Normal | 30 | 2.4318 | 4 | Not Available.
81 | Demineralisation Plant SDL1 | DS1 Slight | no | Lognormal | 0.27 | 0 | 0.2 | 0.1 | 1 | NA | null | null | Normal | 5 | 0.18239 | 0.3 | Using MH Hazus Table 8.3 Small Water Treatment Plant Anchored asuming HAZUS equivalent to 0.3g design level.
82 | Demineralisation Plant SDL1 | DS2 Moderate | no | Lognormal | 0.42 | 0 | 0.35 | 0.3 | 0 | NA | null | null | Normal | 10 | 1.2159 | 2 | Not Available.
83 | Demineralisation Plant SDL1 | DS3 Extensive | no | Lognormal | 0.63 | 0 | 0.4 | 0.75 | 0 | NA | null | null | Normal | 21 | 1.8239 | 3 | Not Available.
84 | Demineralisation Plant SDL1 | DS4 Complete | no | Lognormal | 1.18 | 0 | 0.45 | 1 | 0 | NA | null | null | Normal | 42.8571 | 2.4318 | 4 | Not Available.
85 | Electrostatic Precipitator SDL1 | DS1 Slight | no | Lognormal | 0.28 | 0 | 0.4 | 0.1 | 0 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Assume vulnerability for slight and moderate dominated by high voltage electrical equipment. Use MH HAZUS Table D8.8 for Electrical Equipment Anchored assumed to equate with 0.3g
86 | Electrostatic Precipitator SDL1 | DS2 Moderate | no | Lognormal | 0.45 | 0 | 0.5 | 0.3 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | Assume vulnerability for slight and moderate dominated by high voltage electrical equipment. Use MH HAZUS Table D8.8 for Electrical Equipment Anchored assumed to equate with 0.3g
87 | Electrostatic Precipitator SDL1 | DS3 Extensive | no | Lognormal | 0.6 | 0 | 0.4 | 0.75 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Sim to main feed conveyor
88 | Electrostatic Precipitator SDL1 | DS4 Complete | no | Lognormal | 0.85 | 0 | 0.4 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Sim to main feed conveyor
89 | Fresh Water Supply SDL1 | DS1 Slight | no | Lognormal | 0.27 | 0 | 0.2 | 0.1 | 1 | NA | null | null | Normal | 1 | 0.12159 | 0.2 | Using MH Hazus Table 8.3 Small Pumping Plant Anchored asuming HAZUS equivalent to 0.3g design level.
90 | Fresh Water Supply SDL1 | DS2 Moderate | no | Lognormal | 0.42 | 0 | 0.35 | 0.3 | 0 | NA | null | null | Normal | 4 | 0.30398 | 0.5 | Not Available.
91 | Fresh Water Supply SDL1 | DS3 Extensive | no | Lognormal | 0.63 | 0 | 0.4 | 0.75 | 0 | NA | null | null | Normal | 8 | 0.91194 | 1.5 | Not Available.
92 | Fresh Water Supply SDL1 | DS4 Complete | no | Lognormal | 1.18 | 0 | 0.45 | 1 | 0 | NA | null | null | Normal | 12 | 1.8239 | 3 | Not Available.
93 | Generator SDL1 | DS1 Slight | no | Lognormal | 0.65 | 0 | 0.28 | 0.03 | 0 | NA | null | null | Normal | 3 | 0.60796 | 1 | Not Available.
94 | Generator SDL1 | DS2 Moderate | no | Lognormal | 0.9 | 0 | 0.3 | 0.15 | 0 | NA | null | null | Normal | 20 | 1.2159 | 2 | Not Available.
95 | Generator SDL1 | DS3 Extensive | no | Lognormal | 1.23 | 0 | 0.34 | 0.4 | 0 | NA | null | null | Normal | 60 | 2.4318 | 4 | Using MH HAZUS Table D8.8 for Motor Driven Pumps anchored assuming HAZUS equivalent to 0.3g design level - Extensive.
96 | Generator SDL1 | DS4 Complete | no | Lognormal | 1.45 | 0 | 0.28 | 1.2 | 0 | NA | null | null | Normal | 102.8571 | 4.8637 | 8 | Not Available.
97 | Main Feed Conveyor SDL1 | DS1 Slight | no | Lognormal | 0.28 | 0 | 0.25 | 0.06 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Not Available.
98 | Main Feed Conveyor SDL1 | DS2 Moderate | no | Lognormal | 0.43 | 0 | 0.35 | 0.3 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | Not Available.
99 | Main Feed Conveyor SDL1 | DS3 Extensive | no | Lognormal | 0.6 | 0 | 0.4 | 0.75 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
100 | Main Feed Conveyor SDL1 | DS4 Complete | no | Lognormal | 0.85 | 0 | 0.4 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
101 | Power House SDL1 | DS1 Slight | no | Lognormal | 0.28 | 0 | 0.25 | 0.06 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Not Available.
102 | Power House SDL1 | DS2 Moderate | no | Lognormal | 0.43 | 0 | 0.35 | 0.3 | 1 | NA | null | null | Normal | 17 | 0.60796 | 1 | Not Available.
103 | Power House SDL1 | DS3 Extensive | no | Lognormal | 0.6 | 0 | 0.4 | 0.75 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
104 | Power House SDL1 | DS4 Complete | no | Lognormal | 0.85 | 0 | 0.4 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
105 | Stack SDL1 | DS1 Slight | no | Lognormal | 0.67 | 0 | 0.2 | 0.1 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Wind dominance to effective desing resistance of 0.6g
106 | Stack SDL1 | DS2 Moderate | no | Lognormal | 0.85 | 0 | 0.27 | 0.4 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | Not Available.
107 | Stack SDL1 | DS3 Extensive | no | Lognormal | 1.05 | 0 | 0.35 | 0.8 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
108 | Stack SDL1 | DS4 Complete | no | Lognormal | 1.35 | 0 | 0.35 | 1.2 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
109 | Stacker Reclaimer SDL1 | DS1 Slight | no | Lognormal | 0.3 | 0 | 0.5 | 0.06 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Not Available.
110 | Stacker Reclaimer SDL1 | DS2 Moderate | no | Lognormal | 0.5 | 0 | 0.6 | 0.2 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2 as reference for moderate damage for 0.3g design level.
111 | Stacker Reclaimer SDL1 | DS3 Extensive | no | Lognormal | 0.7 | 0 | 0.55 | 0.8 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
112 | Stacker Reclaimer SDL1 | DS4 Complete | no | Lognormal | 0.9 | 0 | 0.46 | 1.2 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
113 | Stepup Transformer SDL1 | DS1 Slight | no | Lognormal | 0.4 | 0 | 0.45 | 0.03 | 0 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Assume Syner G Table 3.22 230kV with Anchored Sub Components represents 0.3g design level.
114 | Stepup Transformer SDL1 | DS2 Moderate | no | Lognormal | 0.75 | 0 | 0.32 | 0.1 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | Not Available.
115 | Stepup Transformer SDL1 | DS3 Extensive | no | Lognormal | 1.1 | 0 | 0.27 | 0.15 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
116 | Stepup Transformer SDL1 | DS4 Complete | no | Lognormal | 1.5 | 0 | 0.17 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
117 | Supply Conveyor SDL1 | DS1 Slight | no | Lognormal | 0.24 | 0 | 0.3 | 0.1 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Similar to main conveyor but with greater variability.
118 | Supply Conveyor SDL1 | DS2 Moderate | no | Lognormal | 0.42 | 0 | 0.37 | 0.4 | 1 | NA | null | null | Normal | 17 | 0.60796 | 1 | Not Available.
119 | Supply Conveyor SDL1 | DS3 Extensive | no | Lognormal | 0.6 | 0 | 0.45 | 0.8 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
120 | Supply Conveyor SDL1 | DS4 Complete | no | Lognormal | 0.85 | 0 | 0.45 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
121 | Turbine and Condenser SDL1 | DS1 Slight | no | Lognormal | 0.6 | 0 | 0.28 | 0.1 | 0 | NA | null | null | Normal | 5 | 0.60796 | 1 | Using MH Hazus Table D8.8 for Motor Driven Pumps anchored assuming HAZUS equivalent to 0.3g design level - Extensive.
122 | Turbine and Condenser SDL1 | DS2 Moderate | no | Lognormal | 0.8 | 0 | 0.3 | 0.3 | 0 | NA | null | null | Normal | 20 | 1.2159 | 2 | Not Available.
123 | Turbine and Condenser SDL1 | DS3 Extensive | no | Lognormal | 1.18 | 0 | 0.34 | 0.85 | 0 | NA | null | null | Normal | 50 | 2.4318 | 4 | Not Available.
124 | Turbine and Condenser SDL1 | DS4 Complete | no | Lognormal | 1.4 | 0 | 0.28 | 1.2 | 0 | NA | null | null | Normal | 102.8571 | 4.8637 | 8 | Not Available.
125 | Unloader SDL1 | DS1 Slight | no | Lognormal | 0.3 | 0 | 0.5 | 0.06 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Not Available.
126 | Unloader SDL1 | DS2 Moderate | no | Lognormal | 0.5 | 0 | 0.6 | 0.2 | 0.6 | NA | null | null | Normal | 17 | 0.60796 | 1 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2 as reference for moderate damage for 0.3g design level.
127 | Unloader SDL1 | DS3 Extensive | no | Lognormal | 0.7 | 0 | 0.55 | 0.8 | 0.2 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
128 | Unloader SDL1 | DS4 Complete | no | Lognormal | 0.9 | 0 | 0.46 | 1.2 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
129 | Ash Disposal System SDL3 | DS1 Slight | no | Lognormal | 0.37 | 0 | 0.27 | 0.05 | 1 | NA | null | null | Normal | 0.2 | 0.060796 | 0.1 | SIM to supply conveyor
130 | Ash Disposal System SDL3 | DS2 Moderate | no | Lognormal | 0.55 | 0 | 0.32 | 0.3 | 0 | NA | null | null | Normal | 0.5 | 0.060796 | 0.1 | SIM to supply conveyor
131 | Ash Disposal System SDL3 | DS3 Extensive | no | Lognormal | 0.75 | 0 | 0.42 | 0.75 | 0 | NA | null | null | Normal | 1 | 0.30398 | 0.5 | SIM to supply conveyor
132 | Ash Disposal System SDL3 | DS4 Complete | no | Lognormal | 1.05 | 0 | 0.46 | 1 | 0 | NA | null | null | Normal | 4.3 | 0.60796 | 1 | SIM to supply conveyor
133 | Boiler SDL3 | DS1 Slight | no | Lognormal | 0.4 | 0 | 0.55 | 0.1 | 1 | NA | null | null | Normal | 3 | 0.60796 | 1 | Not Available.
134 | Boiler SDL3 | DS2 Moderate | no | Lognormal | 0.62 | 0 | 0.65 | 0.3 | 0 | NA | null | null | Normal | 20 | 1.2159 | 2 | Not Available.
135 | Boiler SDL3 | DS3 Extensive | no | Lognormal | 0.95 | 0 | 0.6 | 0.9 | 0 | NA | null | null | Normal | 60 | 2.4318 | 4 | Not Available.
136 | Boiler SDL3 | DS4 Complete | no | Lognormal | 1.9 | 0 | 0.65 | 1.3 | 0 | NA | null | null | Normal | 102.8571 | 2.4318 | 4 | Not Available.
137 | Coal Yard SDL3 | DS1 Slight | no | Lognormal | 0.67 | 0 | 0.2 | 0.06 | 1 | NA | null | null | Normal | 0.2 | 0.060796 | 0.1 | Not Available.
138 | Coal Yard SDL3 | DS2 Moderate | no | Lognormal | 0.85 | 0 | 0.27 | 0.3 | 1 | NA | null | null | Normal | 0.5 | 0.060796 | 0.1 | Not Available.
139 | Coal Yard SDL3 | DS3 Extensive | no | Lognormal | 1.05 | 0 | 0.35 | 0.75 | 0 | NA | null | null | Normal | 1 | 0.30398 | 0.5 | Not Available.
140 | Coal Yard SDL3 | DS4 Complete | no | Lognormal | 1.35 | 0 | 0.35 | 1 | 0 | NA | null | null | Normal | 4.3 | 0.60796 | 1 | Not Available.
141 | Cooling System SDL3 | DS1 Slight | no | Lognormal | 0.47 | 0 | 0.35 | 0.1 | 1 | NA | null | null | Normal | 1 | 0.30398 | 0.5 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
142 | Cooling System SDL3 | DS2 Moderate | no | Lognormal | 0.62 | 0 | 0.35 | 0.3 | 0 | NA | null | null | Normal | 3 | 0.60796 | 1 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
143 | Cooling System SDL3 | DS3 Extensive | no | Lognormal | 0.83 | 0 | 0.45 | 0.75 | 0 | NA | null | null | Normal | 15 | 1.8239 | 3 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
144 | Cooling System SDL3 | DS4 Complete | no | Lognormal | 1.38 | 0 | 0.45 | 1 | 0 | NA | null | null | Normal | 30 | 2.4318 | 4 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
145 | Demineralisation Plant SDL3 | DS1 Slight | no | Lognormal | 0.35 | 0 | 0.5 | 0.1 | 1 | NA | null | null | Normal | 5 | 0.18239 | 0.3 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
146 | Demineralisation Plant SDL3 | DS2 Moderate | no | Lognormal | 0.48 | 0 | 0.5 | 0.3 | 0 | NA | null | null | Normal | 10 | 1.2159 | 2 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
147 | Demineralisation Plant SDL3 | DS3 Extensive | no | Lognormal | 0.63 | 0 | 0.6 | 0.75 | 0 | NA | null | null | Normal | 21 | 1.8239 | 3 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
148 | Demineralisation Plant SDL3 | DS4 Complete | no | Lognormal | 0.93 | 0 | 0.6 | 1 | 0 | NA | null | null | Normal | 42.8571 | 2.4318 | 4 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
149 | Electrostatic Precipitator SDL3 | DS1 Slight | no | Lognormal | 0.35 | 0 | 0.5 | 0.1 | 0 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | HAZUS-MH Table D8.8 Electircal equipment
150 | Electrostatic Precipitator SDL3 | DS2 Moderate | no | Lognormal | 0.48 | 0 | 0.5 | 0.3 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | HAZUS-MH Table D8.8 Electircal equipment
151 | Electrostatic Precipitator SDL3 | DS3 Extensive | no | Lognormal | 0.63 | 0 | 0.6 | 0.75 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Sim to main feed conveyor
152 | Electrostatic Precipitator SDL3 | DS4 Complete | no | Lognormal | 0.93 | 0 | 0.6 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Sim to main feed conveyor
153 | Fresh Water Supply SDL3 | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.7 | 0.1 | 1 | NA | null | null | Normal | 1 | 0.12159 | 0.2 | HAZUS-MH MR3 Table 8.6 Small Pumping Plants
154 | Fresh Water Supply SDL3 | DS2 Moderate | no | Lognormal | 0.46 | 0 | 0.65 | 0.3 | 0 | NA | null | null | Normal | 4 | 0.30398 | 0.5 | Not Available.
155 | Fresh Water Supply SDL3 | DS3 Extensive | no | Lognormal | 0.76 | 0 | 0.65 | 0.75 | 0 | NA | null | null | Normal | 8 | 0.91194 | 1.5 | Not Available.
156 | Fresh Water Supply SDL3 | DS4 Complete | no | Lognormal | 1.6 | 0 | 0.8 | 1 | 0 | NA | null | null | Normal | 12 | 1.8239 | 3 | Not Available.
157 | Generator SDL3 | DS1 Slight | no | Lognormal | 0.8 | 0 | 0.28 | 0.03 | 0 | NA | null | null | Normal | 3 | 0.60796 | 1 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
158 | Generator SDL3 | DS2 Moderate | no | Lognormal | 1.05 | 0 | 0.3 | 0.15 | 0 | NA | null | null | Normal | 20 | 1.2159 | 2 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
159 | Generator SDL3 | DS3 Extensive | no | Lognormal | 1.38 | 0 | 0.34 | 0.4 | 0 | NA | null | null | Normal | 60 | 2.4318 | 4 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
160 | Generator SDL3 | DS4 Complete | no | Lognormal | 1.6 | 0 | 0.28 | 1.2 | 0 | NA | null | null | Normal | 102.8571 | 4.8637 | 8 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
161 | Main Feed Conveyor SDL3 | DS1 Slight | no | Lognormal | 0.37 | 0 | 0.21 | 0.06 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Not Available.
162 | Main Feed Conveyor SDL3 | DS2 Moderate | no | Lognormal | 0.55 | 0 | 0.26 | 0.3 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | Not Available.
163 | Main Feed Conveyor SDL3 | DS3 Extensive | no | Lognormal | 0.75 | 0 | 0.36 | 0.75 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
164 | Main Feed Conveyor SDL3 | DS4 Complete | no | Lognormal | 1.05 | 0 | 0.4 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
165 | Power House SDL3 | DS1 Slight | no | Lognormal | 0.27 | 0 | 0.25 | 0.06 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Not Available.
166 | Power House SDL3 | DS2 Moderate | no | Lognormal | 0.45 | 0 | 0.32 | 0.3 | 1 | NA | null | null | Normal | 17 | 0.60796 | 1 | Not Available.
167 | Power House SDL3 | DS3 Extensive | no | Lognormal | 0.65 | 0 | 0.4 | 0.75 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
168 | Power House SDL3 | DS4 Complete | no | Lognormal | 0.95 | 0 | 0.4 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
169 | Stack SDL3 | DS1 Slight | no | Lognormal | 0.67 | 0 | 0.2 | 0.1 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Not Available.
170 | Stack SDL3 | DS2 Moderate | no | Lognormal | 0.85 | 0 | 0.27 | 0.4 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | Not Available.
171 | Stack SDL3 | DS3 Extensive | no | Lognormal | 1.05 | 0 | 0.35 | 0.8 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
172 | Stack SDL3 | DS4 Complete | no | Lognormal | 1.35 | 0 | 0.35 | 1.2 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
173 | Stacker Reclaimer SDL3 | DS1 Slight | no | Lognormal | 0.4 | 0 | 0.5 | 0.06 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
174 | Stacker Reclaimer SDL3 | DS2 Moderate | no | Lognormal | 0.6 | 0 | 0.6 | 0.2 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
175 | Stacker Reclaimer SDL3 | DS3 Extensive | no | Lognormal | 0.8 | 0 | 0.55 | 0.8 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
176 | Stacker Reclaimer SDL3 | DS4 Complete | no | Lognormal | 1 | 0 | 0.46 | 1.2 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
177 | Stepup Transformer SDL3 | DS1 Slight | no | Lognormal | 0.6 | 0 | 0.32 | 0.03 | 0 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
178 | Stepup Transformer SDL3 | DS2 Moderate | no | Lognormal | 0.95 | 0 | 0.24 | 0.1 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
179 | Stepup Transformer SDL3 | DS3 Extensive | no | Lognormal | 1.3 | 0 | 0.19 | 0.15 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
180 | Stepup Transformer SDL3 | DS4 Complete | no | Lognormal | 1.7 | 0 | 0.09 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
181 | Supply Conveyor SDL3 | DS1 Slight | no | Lognormal | 0.37 | 0 | 0.27 | 0.1 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Not Available.
182 | Supply Conveyor SDL3 | DS2 Moderate | no | Lognormal | 0.55 | 0 | 0.32 | 0.4 | 1 | NA | null | null | Normal | 17 | 0.60796 | 1 | Not Available.
183 | Supply Conveyor SDL3 | DS3 Extensive | no | Lognormal | 0.85 | 0 | 0.42 | 0.8 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
184 | Supply Conveyor SDL3 | DS4 Complete | no | Lognormal | 1.05 | 0 | 0.46 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
185 | Turbine and Condenser SDL3 | DS1 Slight | no | Lognormal | 0.8 | 0 | 0.28 | 0.1 | 0 | NA | null | null | Normal | 5 | 0.60796 | 1 | Not Available.
186 | Turbine and Condenser SDL3 | DS2 Moderate | no | Lognormal | 1.05 | 0 | 0.3 | 0.3 | 0 | NA | null | null | Normal | 20 | 1.2159 | 2 | Not Available.
187 | Turbine and Condenser SDL3 | DS3 Extensive | no | Lognormal | 1.38 | 0 | 0.34 | 0.85 | 0 | NA | null | null | Normal | 50 | 2.4318 | 4 | Not Available.
188 | Turbine and Condenser SDL3 | DS4 Complete | no | Lognormal | 1.6 | 0 | 0.28 | 1.2 | 0 | NA | null | null | Normal | 102.8571 | 4.8637 | 8 | Not Available.
189 | Unloader SDL3 | DS1 Slight | no | Lognormal | 0.5 | 0 | 0.5 | 0.06 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
190 | Unloader SDL3 | DS2 Moderate | no | Lognormal | 0.7 | 0 | 0.6 | 0.2 | 0.6 | NA | null | null | Normal | 17 | 0.60796 | 1 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
191 | Unloader SDL3 | DS3 Extensive | no | Lognormal | 0.9 | 0 | 0.55 | 0.8 | 0.2 | NA | null | null | Normal | 37 | 1.2159 | 2 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
192 | Unloader SDL3 | DS4 Complete | no | Lognormal | 1.1 | 0 | 0.46 | 1.2 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
193 | Switch Yard | DS1 Slight | no | Lognormal | 0.11 | 0 | 0.7 | 0.3 | 1 | NA | null | null | Normal | 1 | 0.30398 | 0.5 | HAZUS-MH MR3 Table 8.22.a Substations
194 | Switch Yard | DS2 Moderate | no | Lognormal | 0.15 | 0 | 0.75 | 0.6 | 0.6 | NA | null | null | Normal | 3 | 0.91194 | 1.5 | HAZUS-MH MR3 Table 8.22.a Substations
195 | Switch Yard | DS3 Extensive | no | Lognormal | 0.2 | 0 | 0.75 | 0.8 | 0.2 | NA | null | null | Normal | 7 | 2.1278 | 3.5 | HAZUS-MH MR3 Table 8.22.a Substations
196 | Switch Yard | DS4 Complete | no | Lognormal | 0.47 | 0 | 0.7 | 1 | 0 | NA | null | null | Normal | 30 | 9.1194 | 15 | HAZUS-MH MR3 Table 8.22.a Substations
197 | SYSTEM_OUTPUT | DS1 Slight | no | Lognormal | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.
198 | SYSTEM_OUTPUT | DS2 Moderate | no | Lognormal | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.
199 | SYSTEM_OUTPUT | DS3 Extensive | no | Lognormal | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.
200 | SYSTEM_OUTPUT | DS4 Complete | no | Lognormal | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.
201 | SYSTEM_INPUT | DS1 Slight | no | Lognormal | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.
202 | SYSTEM_INPUT | DS2 Moderate | no | Lognormal | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.
203 | SYSTEM_INPUT | DS3 Extensive | no | Lognormal | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.
204 | SYSTEM_INPUT | DS4 Complete | no | Lognormal | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.

## damage_state_def
component_type | damage_state | damage_state_definition
Ash Disposal System | DS1 Slight | Minor deformation to supporting structure with some yielding of hold-down bolts.
Ash Disposal System | DS2 Moderate | Significant deformaton to steel supporting structure with misaligment of ash handling conveyors
Ash Disposal System | DS3 Extensive | Horizontal displacement of structure with failure of bracing elements and damage to ash silo structure.
Ash Disposal System | DS4 Complete | Partial or complete collapse of ash handling system.
Boiler | DS1 Slight | Minor deformation to supporting structure and minor damage at lateral restraint points to boiler. No internal damage to boiler.
Boiler | DS2 Moderate | Significant deformation to supporting structure with deformation at holding down bolts and yielding of bracing elements. Damage to internal boiler pipes requiring access for repair.
Boiler | DS3 Extensive | Major damage to boiler support with failure of many bracing elements. Large deformations damage connecting pipework. Widespread damage to internal steam pipes in boiler requring extensive replacement.
Boiler | DS4 Complete | Damage beyond repair
Coal Yard | DS1 Slight | Minor deformations in connections or hairline cracks in a few welds. Minor brace deformation. Some deformation at hold down bolts.
Coal Yard | DS2 Moderate | Some steel members have yielded exhibiting observable permanent rotations at connections. A few welded connections may exhibit major cracks through welds or a few bolted connections may exhibit broken bolts or enlarged bolt holes. Some yielding of braces and soem anchor bolts stretched.
Coal Yard | DS3 Extensive | Many steel bracing elements have exceeded their yield capacity resulting in significant permanent lateral deformation of the structure. Many truss arch members have buckeld in compression. Some of the structural connections may have exceeded their ultimate capacity exhibited by major permanent member rotations at connections, buckled flanges and failed connections. Some foundation oviement due to settlement and some anchor bolts failed.
Coal Yard | DS4 Complete | A significant proportion of the structural elements have exceeded their ultimate capacities or some critical structural elements or connections have failed resulting in dangerous permanent lateral displacement, partial collapse or collapse of the shelter structure.
Cooling System | DS1 Slight | Minor damage to water handling pumps and pipework. Minor damage to pumphouse superstructure.
Cooling System | DS2 Moderate | Moderate structural damage to pumphouse superstructure. Deformation of pump hold-down and pipework with some leakage at flanges and valves. Some movement of pumphouse substructure due to liquefaction.
Cooling System | DS3 Extensive | Rupture of some water mains due to failure of supporting strucuture. Significant movement of pumps and motors leading to some misalignment. Extensive damage to pumphouse superstructure, power supply and control panels. Movement of pumphouse substructure and other valve chambers leading to damage to water mains.
Cooling System | DS4 Complete | Damage beyond repair.
Demineralisation Plant | DS1 Slight | Minor damage to water handling pumps and pipework. Minor damage to plant superstructure.
Demineralisation Plant | DS2 Moderate | Moderate structural damage to demin plant superstructure. Deformation of pump hold-down and pipework with some leakage at flanges and valves. Some movement of pumphouse substructure due to liquefaction.
Demineralisation Plant | DS3 Extensive | Rupture of some water mains due to failure of supporting strucuture. Significant movement of pumps and motors leading to some misalignment. Extensive damage to demin plant superstructure, power supply and control panels. Movement of demin substructure and other valve chambers significant leading to damage to water mains.
Demineralisation Plant | DS4 Complete | Damage beyond repair.
Electrostatic Precipitator | DS1 Slight | minor damage to supporting structure and electrical equipment
Electrostatic Precipitator | DS2 Moderate | significant deformation to supporting structure. Leakage of flue gases. Some damage to internal discharge electrodes and collector panels.
Electrostatic Precipitator | DS3 Extensive | Major deformation of supporting structure with failure of key bracing elements and permanent offset. Internal discharge electrodes and collector panels extensively damaged. Damage to high voltage power supply and control equipment.
Electrostatic Precipitator | DS4 Complete | Damage beyond repair.
Fresh Water Supply | DS1 Slight | Minor movement of intake structure and minor damage to freshwater pumps and pipework.
Fresh Water Supply | DS2 Moderate | Partial liquefaction of soils in the vicinity of intake structure leading to some horizontal movement and rotation with attendent damage to pipework. Horizontal movement to freshwater pumps and peripheral pipework.
Fresh Water Supply | DS3 Extensive | Extensive liquefaction leading to large scale movement of intake structures with major damage to both pipework and pumping facilities. Control equipment damaged.
Fresh Water Supply | DS4 Complete | Damage beyond repair
Generator | DS1 Slight | Minor damage to generator electrical connectivity. Some horizonrtal deformation to generator support with distortion of holding down bolts.
Generator | DS2 Moderate | Significant horizontal deformation leading to misalignment of generator to turbine shaft.
Generator | DS3 Extensive | Large horizontal deformation of both condensor and turbine relative to supporting plinth leading to damage to generator to turbine shaft requiring replacement.
Generator | DS4 Complete | Irreparable damage to generator.
Main Feed Conveyor | DS1 Slight | Minor deformation of support structure with some yeilding of holding down bolts.
Main Feed Conveyor | DS2 Moderate | Significant deformation of supporting structure with horizontal displacement of conveyor system. Misalignment of feed conveyors.
Main Feed Conveyor | DS3 Extensive | Major damage to supporting structure with failure of bracing elelments. Damage to seating of conveyor structure on supporting frame. Possible permanent drift due to foundation settlement.
Main Feed Conveyor | DS4 Complete | Partial or complete collapse.
Power House | DS1 Slight | Minor deformations in connections or hairline cracks in a few welds. Minor brace deformation. Minor spalling at some precast panel corners.
Power House | DS2 Moderate | Some steel members have yielded exhibiting observable permanent rotations at connections. A few welded connections may exhibit major cracks through welds or a few bolted connections may exhibit broken bolts or enlarged bolt holes. Some yielding of braces. More significant spalling damage to precast panels with deformation at panel connections.
Power House | DS3 Extensive | Most steel members have exceeded their yield capacity resulting in significant permanent lateral deformation of the structure. Some of the structural members or connections may have exceeded their ultimate capacity exhibited by major permanent member rotations at connections, buckled flanges and failed connections. Some anchor bolts stretched. Partial collapse of portions of the structure may have occurred due to failed critical elements or connections.
Power House | DS4 Complete | A significant proportion of the structural elements have exceeded their ultimate capacities or some critical structural elements or connections have failed resulting in dangerous permanent lateral displacement, partial collapse or collapse of the building.
Stack | DS1 Slight | Minor damage to structure with deformation of holding down bolts and with some bracing connections.
Stack | DS2 Moderate | Significant deformation of supporting structure with horizontal displacement. Yielding of bracing elements. Damage to flue leading to gas leakage.
Stack | DS3 Extensive | Major horizontal deformation with permanent drift. Failure of bracing elements and extensive damage to flue with many leakage points.
Stack | DS4 Complete | Damage beyond repair including collapse.
Stacker Reclaimer | DS1 Slight | Minor deformation to rail support and stacker reclaimer bracing elements.
Stacker Reclaimer | DS2 Moderate | Significant deformation of stacker structural elements leading to misalignment of machine components and conveyors.
Stacker Reclaimer | DS3 Extensive | Ground deformation leading to gross movement of support rails. Failure of bracing elements on stacker leading to permanent distortion of equipment. Damage to power supply and control equipment.
Stacker Reclaimer | DS4 Complete | Overturning with major distortion of structural elements.
Stepup Transformer | DS1 Slight | Porcelain Gasket Leak
Stepup Transformer | DS2 Moderate | Porcelain Break, Major break in Radiator
Stepup Transformer | DS3 Extensive | Anchorage Failure
Stepup Transformer | DS4 Complete | Overturn
Supply Conveyor | DS1 Slight | Minor deformation of support structure with some yeilding of holding down bolts.
Supply Conveyor | DS2 Moderate | Significant deformation of supporting structure with horizontal displacement of conveyor system. Misalignment of feed conveyors.
Supply Conveyor | DS3 Extensive | Major damage to supporting structure with failure of bracing elelments. Damage to seating of conveyor structure on supporting frame. Possible permanent drift due to foundation settlement.
Supply Conveyor | DS4 Complete | Partial or complete collapse.
Turbine and Condenser | DS1 Slight | Minor damage to condensor pipework. Some horizontal deformation of condensor support connections and steam supply to turbine.
Turbine and Condenser | DS2 Moderate | Significant horizontal deformation of both condensor and turbine relative to supporting plinth leading to misalignment of turbine shaft to generator and steam leakage in pipework.
Turbine and Condenser | DS3 Extensive | Large horizontal deformation of both condensor and turbine relative to supporting plinth leading to damage to turbine shaft to generator requiring replacement. Internal damage to condensor requiring replacement.
Turbine and Condenser | DS4 Complete | Irreparable damage to turbine and condensor.
Unloader | DS1 Slight | Minor deformation to rail support and unloader bracing frame elements.
Unloader | DS2 Moderate | Significant deformation of unloader structural elements leading to misalignment of machine components and conveyors. Minor derailment from tracks on wharf.
Unloader | DS3 Extensive | Failure of bracing elements on unloader leading to permanent distortion of equipment. Damage to power supply and control equipment. Major derailment.
Unloader | DS4 Complete | Overturning with major distortion of structural elements.
Switch Yard | DS1 Slight
Switch Yard | DS2 Moderate
Switch Yard | DS3 Extensive
Switch Yard | DS4 Complete
SYSTEM_OUTPUT | DS1 Slight
SYSTEM_OUTPUT | DS2 Moderate
SYSTEM_OUTPUT | DS3 Extensive
SYSTEM_OUTPUT | DS4 Complete
SYSTEM_INPUT | DS1 Slight
SYSTEM_INPUT | DS2 Moderate
SYSTEM_INPUT | DS3 Extensive
SYSTEM_INPUT | DS4 Complete

## VALIDATION_TABLES
INFRASTRUCTURE_LEVEL | SYSTEM_CLASSES | RESTORATION_TIME_UNIT | COMPONENT_LOCATION_CONF
facility | PowerStation | days | defined
network | Substation | weeks | undefined
| PotableWaterTreatmentPlant | months | schematic
| PWTP | years | geospatial
WasteWaterTreatmentPlant
WWTP
PotableWaterPumpStation
ElectricPowerNetwork
PotableWaterNetwork
RailNetwork