## system_meta
model_config_param | value | notes
MODEL_NAME | Generic Water Pumping Station
INFRASTRUCTURE_LEVEL | facility
SYSTEM_CLASS | PotableWaterPumpStation
SYSTEM_SUBCLASS | Freshwater Pumping Station
SYSTEM_COMPONENT_LOCATION_CONF | defined
RESTORATION_TIME_UNIT | days
HAZARD_INTENSITY_MEASURE_PARAM | PGA
HAZARD_INTENSITY_MEASURE_UNIT | g

## table_description
Table Name | Description | Note
component_list | This file lists the instances of various component types within the system. Component design level x.xx g. | Cost fractions define economic value of the individual component relative to the cost of entire system. Data includes a __% allowance for components not included in the model.
component_connections | Network connections. Each pair of nodes implies a connecting edge. Directionality is defined by order of nodes in a row (Orig -> Dest). | Used by: (1) network algorithm package for flow calculations, (2) Pygraphviz to draw the system layout.
supply_setup | Necessary input materiél required for plant operation. | Capacity given as percentage.
output_setup | Treatment Capacity in Mega Litres per Day (MLD)
comp_type_dmg_algo | List of component types with fragility and recovery data | Fragilities are defined according to discrete damage states. Recovery time is in DAYS.
damage_state_def | Definitions of damage states of the list of component types in the system

## component_list
component_id | component_type | component_class | cost_fraction | node_type | node_cluster | operating_capacity | pos_x | pos_y | site_id
Water_Supply | SYSTEM_INPUT | MODEL ARTEFACT | 0 | supply | ZONE_01 | 1 | 4 | 5 | 0
Pipe_Main_Inlet | Pipe Main Inlet | Pipework | 0.029696 | transshipment | ZONE_01 | 1 | 10 | 5 | 0
Pumphouse_Inlet_Joint | Pipework Elevated | Pipework | 0.029696 | transshipment | ZONE_01 | 1 | 40 | 5 | 0
Commercial_Power_Supply | SYSTEM_INPUT | MODEL ARTEFACT | 0 | supply | ZONE_02 | 1 | 4 | 25 | 0
Supplier_Connection_Switchboard | Electric Switchboard | Electric Power Equipment | 0.041574 | transshipment | ZONE_02 | 1 | 10 | 25 | 0
Mains_Incomer | Electric Control Panel | Electrical Control Equipment | 0 | transshipment | ZONE_02 | 1 | 15 | 25 | 0
SWITCHROOM_HV | Switchrooms | Building | 0.093541 | dependency | ZONE_02 | 1 | 15 | 30 | 0
Customer_Main_Switchboard | Electric Switchboard | Electric Power Equipment | 0.020787 | transshipment | ZONE_02 | 1 | 20 | 25 | 0
Diesel_Storage_Tank | Diesel Storage Tank Horizontal | Steel Tank | 0.012472 | dependency | ZONE_03 | 1 | 4 | 20 | 0
Standby_Genset_No1 | Backup Genset | Generator | 0.024944 | transshipment | ZONE_03 | 1 | 10 | 20 | 0
Tx_Gen | Transformer Kiosk | Electric Power Equipment | 0.020787 | transshipment | ZONE_03 | 1 | 15 | 20 | 0
Generator_Incomer | Electric Control Panel | Electrical Control Equipment | 0 | transshipment | ZONE_03 | 1 | 20 | 20 | 0
Tx_Aux | Transformer Kiosk | Electric Power Equipment | 0.0083148 | transshipment | ZONE_04 | 1 | 30 | 30 | 0
JUNCTION_AUX | JUNCTION_NODE | MODEL ARTEFACT | 0 | junction | ZONE_04 | 1 | 30 | 35 | 0
Switchboard_LV | Electric Switchboard | Electric Power Equipment | 0.087305 | transshipment | ZONE_04 | 1 | 35 | 30 | 0
Auxiliary_Electrical_Systems | Electric Control Panel | Electrical Control Equipment | 0 | transshipment | ZONE_04 | 1 | 40 | 30 | 0
TRANSFORMER_ROOM | Building Tilt-up Concrete | Building | 0.20787 | dependency | ZONE_05 | 1 | 25 | 10 | 0
Tx_Isolating_No1 | Transformer Dry Type | Electric Power Equipment | 0.020787 | transshipment | ZONE_05 | 1 | 30 | 15 | 0
Tx_Isolating_No2 | Transformer Dry Type | Electric Power Equipment | 0.020787 | transshipment | ZONE_05 | 1 | 30 | 20 | 0
Tx_Isolating_No3 | Transformer Dry Type | Electric Power Equipment | 0.020787 | transshipment | ZONE_05 | 1 | 30 | 25 | 0
PUMP_ROOM | Building Tilt-up Concrete | Building | 0.20787 | dependency | ZONE_06 | 1 | 35 | 10 | 0
Pump_N1 | Pump Horizontal 1500kW | Pump | 0.03118 | transshipment | ZONE_06 | 1 | 45 | 15 | 0
Pump_N2 | Pump Horizontal 1500kW | Pump | 0.03118 | transshipment | ZONE_06 | 1 | 45 | 20 | 0
Pump_N3 | Pump Horizontal 1500kW | Pump | 0.03118 | transshipment | ZONE_06 | 1 | 45 | 25 | 0
Pump_Output_Connector | Pipework Elevated | Pipework | 0.029696 | transshipment | ZONE_06 | 1 | 50 | 20 | 0
Pipe_Main_Outlet | Pipework Elevated | Pipework | 0.029696 | transshipment | ZONE_06 | 1 | 55 | 20 | 0
Output_Freshwater | SYSTEM_OUTPUT | MODEL ARTEFACT | 0 | sink | ZONE_07 | 1 | 60 | 20 | 0

## component_connections
origin | destination | link_capacity | weight
Commercial_Power_Supply | Supplier_Connection_Switchboard | 1 | 1
Supplier_Connection_Switchboard | Mains_Incomer | 1 | 1
Mains_Incomer | Customer_Main_Switchboard | 1 | 1
SWITCHROOM_HV | Supplier_Connection_Switchboard | 1 | 1
SWITCHROOM_HV | Customer_Main_Switchboard | 1 | 1
SWITCHROOM_HV | Mains_Incomer | 1 | 1
Customer_Main_Switchboard | Tx_Aux | 1 | 1
Diesel_Storage_Tank | Standby_Genset_No1 | 1 | 1
Standby_Genset_No1 | Tx_Gen | 1 | 1
Tx_Gen | Generator_Incomer | 1 | 1
Generator_Incomer | Customer_Main_Switchboard | 1 | 1
Customer_Main_Switchboard | Tx_Isolating_No1 | 1 | 1
Customer_Main_Switchboard | Tx_Isolating_No2 | 1 | 1
Customer_Main_Switchboard | Tx_Isolating_No3 | 1 | 1
TRANSFORMER_ROOM | Tx_Isolating_No1 | 1 | 1
TRANSFORMER_ROOM | Tx_Isolating_No2 | 1 | 1
TRANSFORMER_ROOM | Tx_Isolating_No3 | 1 | 1
Tx_Isolating_No1 | Pump_N1 | 1 | 1
Tx_Isolating_No2 | Pump_N2 | 1 | 1
Tx_Isolating_No3 | Pump_N3 | 1 | 1
Customer_Main_Switchboard | Tx_Aux | 1 | 1
Tx_Aux | Switchboard_LV | 1 | 1
Switchboard_LV | Auxiliary_Electrical_Systems | 1 | 1
Auxiliary_Electrical_Systems | JUNCTION_AUX | 1 | 1
JUNCTION_AUX | Customer_Main_Switchboard | 1 | 1
Auxiliary_Electrical_Systems | Pump_N1 | 1 | 1
Auxiliary_Electrical_Systems | Pump_N2 | 1 | 1
Auxiliary_Electrical_Systems | Pump_N3 | 1 | 1
Water_Supply | Pipe_Main_Inlet | 1 | 1
Pipe_Main_Inlet | Pumphouse_Inlet_Joint | 1 | 1
Pumphouse_Inlet_Joint | Pump_N1 | 1 | 1
Pumphouse_Inlet_Joint | Pump_N2 | 1 | 1
Pumphouse_Inlet_Joint | Pump_N3 | 1 | 1
PUMP_ROOM | Pump_N1 | 1 | 1
PUMP_ROOM | Pump_N2 | 1 | 1
PUMP_ROOM | Pump_N3 | 1 | 1
Pump_N1 | Pump_Output_Connector | 1 | 1
Pump_N2 | Pump_Output_Connector | 1 | 1
Pump_N3 | Pump_Output_Connector | 1 | 1
Pump_Output_Connector | Pipe_Main_Outlet | 1 | 1
Pipe_Main_Outlet | Output_Freshwater | 1 | 1

## supply_setup
input_node | input_capacity | capacity_fraction | commodity_type
Water_Supply | 100 | 1 | Untreated Water
Commercial_Power_Supply | 100 | 1 | Electric Power

## output_setup
output_node | production_node | output_node_capacity | capacity_fraction | priority
Output_Freshwater | Pipe_Main_Outlet | 150 | 1 | 1

## comp_type_dmg_algo
id | component_type | damage_state | is_piecewise | damage_function | median | beta | location | damage_ratio | functionality | minimum | upper_limit | lower_limit | recovery_function | recovery_param1 | recovery_param2 | recovery_95percentile | data_source | notes
1 | Air Tank Vertical | DS1 Slight | no | Lognormal | 0.18 | 0 | 0.5 | NA | null | null | 0.02 | 0.95 | Normal | 1.671 | 0.2 | 2 | Expert Judgment
2 | Air Tank Vertical | DS2 Moderate | no | Lognormal | 0.362 | 0 | 0.5 | NA | null | null | 0.05 | 0.75 | Normal | 1.671 | 0.2 | 2 | Expert Judgment
3 | Air Tank Vertical | DS3 Extensive | no | Lognormal | 0.9 | 0 | 0.5 | NA | null | null | 0.5 | 0.3 | Normal | 4.1776 | 0.5 | 5 | Expert Judgment
4 | Air Tank Vertical | DS4 Complete | no | Lognormal | 1 | 0 | 0.5 | NA | null | null | 1 | 0 | Normal | 8.3551 | 1 | 10 | Expert Judgment
5 | Building Tilt-up Concrete | DS1 Slight | no | Lognormal | 0.23 | 0 | 0.25 | NA | null | null | 0.01 | 0.95 | Normal | 0.083551 | 0.01 | 0.1 | Algorithm based on fragility for Philippines Power House, adjusted to 0.15g
6 | Building Tilt-up Concrete | DS2 Moderate | no | Lognormal | 0.38 | 0 | 0.35 | NA | null | null | 0.05 | 0.75 | Normal | 0.1671 | 0.02 | 0.2
7 | Building Tilt-up Concrete | DS3 Extensive | no | Lognormal | 0.55 | 0 | 0.4 | NA | null | null | 0.3 | 0.3 | Normal | 4.1776 | 0.5 | 5
8 | Building Tilt-up Concrete | DS4 Complete | no | Lognormal | 0.8 | 0 | 0.4 | NA | null | null | 1 | 0 | Normal | 8.3551 | 1 | 10
9 | Chemical Building | DS1 Slight | no | Lognormal | 0.23 | 0 | 0.25 | NA | null | null | 0.01 | 0.95 | Normal | 0.083551 | 0.01 | 0.1 | Assigned fragility of algorithm for: `Building Tilt-up Concrete`
10 | Chemical Building | DS2 Moderate | no | Lognormal | 0.38 | 0 | 0.35 | NA | null | null | 0.05 | 0.75 | Normal | 0.1671 | 0.02 | 0.2
11 | Chemical Building | DS3 Extensive | no | Lognormal | 0.55 | 0 | 0.4 | NA | null | null | 0.3 | 0.3 | Normal | 4.1776 | 0.5 | 5
12 | Chemical Building | DS4 Complete | no | Lognormal | 0.8 | 0 | 0.4 | NA | null | null | 1 | 0 | Normal | 8.3551 | 1 | 10
13 | Chemical Dosing Panel | DS1 Slight | no | Lognormal | 0.15 | 0 | 0.5 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | Based on HAZUS curves for `Chlorination Equipment`. | Shifted to the right and steepened due to poor base fixity. Moderate damage much less likely.
14 | Chemical Dosing Panel | DS2 Moderate | no | Lognormal | 0.7 | 0 | 0.7 | NA | null | null | 0.05 | 0.75 | Normal | 0.83551 | 0.1 | 1
15 | Chemical Dosing Panel | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 1 | 0.3 | Normal | 83.5515 | 10 | 100
16 | Chemical Dosing Panel | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 1 | 0 | Normal | 125.3272 | 15 | 150
17 | Electric Control Panel | DS1 Slight | no | Lognormal | 0.15 | 0 | 0.5 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | Based on HAZUS curves for `Chlorination Equipment`. | Shifted to the right and steepened due to poor base fixity. Moderate damage much less likely.
18 | Electric Control Panel | DS2 Moderate | no | Lognormal | 0.7 | 0 | 0.7 | NA | null | null | 0.05 | 0.75 | Normal | 1.671 | 0.2 | 2
19 | Electric Control Panel | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 1 | 0.3 | Normal | 83.5515 | 10 | 100
20 | Electric Control Panel | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 1 | 0 | Normal | 125.3272 | 15 | 150
21 | Chemical Tanks PE | DS1 Slight | no | Lognormal | 0.09 | 0 | 0.5 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | GA adaptation of HAZUS algorithm for `Steel Tank Above Ground`. | Median shift 0.05 OA. Moderate 0.2g additional shift. Extensive and Complete 0.4g additional shift left.
22 | Chemical Tanks PE | DS2 Moderate | no | Lognormal | 0.18 | 0 | 0.5 | NA | null | null | 0.05 | 0.75 | Normal | 0.83551 | 0.1 | 1
23 | Chemical Tanks PE | DS3 Extensive | no | Lognormal | 0.35 | 0 | 0.6 | NA | null | null | 1 | 0.3 | Normal | 50.1309 | 6 | 60
24 | Chemical Tanks PE | DS4 Complete | no | Lognormal | 0.6 | 0 | 0.6 | NA | null | null | 1 | 0 | Normal | 50.1309 | 6 | 60
25 | Chlorination Equipment | DS1 Slight | no | Lognormal | 0.23 | 0 | 0.25 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | Assigned fragility of algorithm for: `Building Tilt-up Concrete`
26 | Chlorination Equipment | DS2 Moderate | no | Lognormal | 0.38 | 0 | 0.35 | NA | null | null | 0.05 | 0.75 | Normal | 1.671 | 0.2 | 2
27 | Chlorination Equipment | DS3 Extensive | no | Lognormal | 0.55 | 0 | 0.4 | NA | null | null | 1 | 0.3 | Normal | 4.1776 | 0.5 | 5
28 | Chlorination Equipment | DS4 Complete | no | Lognormal | 0.8 | 0 | 0.4 | NA | null | null | 1 | 0 | Normal | 8.3551 | 1 | 10
29 | Diesel Storage Tank Horizontal | DS1 Slight | no | Lognormal | 0.14 | 0 | 0.5 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | GA adaptation of HAZUS algorithm for `Chlorination Equipment`. NIBS 2003, Table A.8.6, Table 15B.5. | Shifted slightly to right and steepened due to absence of base fixity. Extensive damage much less likely as tank will not overturn and slide as rigid body.
30 | Diesel Storage Tank Horizontal | DS2 Moderate | no | Lognormal | 0.27 | 0 | 0.5 | NA | null | null | 0.05 | 0.75 | Normal | 1.671 | 0.2 | 2
31 | Diesel Storage Tank Horizontal | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 1 | 0.3 | Normal | 4.1776 | 0.5 | 5
32 | Diesel Storage Tank Horizontal | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 1 | 0 | Normal | 4.1776 | 0.5 | 5
33 | Electric Power Commercial | DS1 Slight | no | Lognormal | 0.15 | 0 | 0.4 | NA | null | null | 0.01 | 0.95 | Normal | 1.671 | 0.2 | 2 | Based on HAZUS Unanchored Switchroom. Building 1.5g for Extensive and Complete.
34 | Electric Power Commercial | DS2 Moderate | no | Lognormal | 0.3 | 0 | 0.4 | NA | null | null | 0.05 | 0.75 | Normal | 4.1776 | 0.5 | 5
35 | Electric Power Commercial | DS3 Extensive | no | Lognormal | 0.55 | 0 | 0.4 | NA | null | null | 0.5 | 0.3 | Normal | 8.3551 | 1 | 10
36 | Electric Power Commercial | DS4 Complete | no | Lognormal | 0.8 | 0 | 0.4 | NA | null | null | 0.8 | 0 | Normal | 16.7103 | 2 | 20
37 | Electrical Kiosk Switchroom | DS1 Slight | no | Lognormal | 0.4 | 0 | 0.6 | NA | null | null | 0.02 | 0.95 | Normal | 0.83551 | 0.1 | 1 | NA
38 | Electrical Kiosk Switchroom | DS2 Moderate | no | Lognormal | 0.67 | 0 | 0.7 | NA | null | null | 0.1 | 0.75 | Normal | 1.671 | 0.2 | 2
39 | Electrical Kiosk Switchroom | DS3 Extensive | no | Lognormal | 0.85 | 0 | 0.7 | NA | null | null | 1 | 0.3 | Normal | 4.1776 | 0.5 | 5
40 | Electrical Kiosk Switchroom | DS4 Complete | no | Lognormal | 1 | 0 | 0.7 | NA | null | null | 1 | 0 | Normal | 8.3551 | 1 | 10
41 | Electric Switchboard | DS1 Slight | no | Lognormal | 0.4 | 0 | 0.6 | NA | null | null | 0.02 | 0.95 | Normal | 0.83551 | 0.1 | 1 | Nominally assigned the same attributes as Electrical Kiosk Switchroom
42 | Electric Switchboard | DS2 Moderate | no | Lognormal | 0.67 | 0 | 0.7 | NA | null | null | 0.1 | 0.75 | Normal | 1.671 | 0.2 | 2
43 | Electric Switchboard | DS3 Extensive | no | Lognormal | 0.85 | 0 | 0.7 | NA | null | null | 1 | 0.3 | Normal | 4.1776 | 0.5 | 5
44 | Electric Switchboard | DS4 Complete | no | Lognormal | 1 | 0 | 0.7 | NA | null | null | 1 | 0 | Normal | 8.3551 | 1 | 10
45 | Pipework Elevated | DS1 Slight | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | HAZUS algorithms for `Eleveted Pipes - Anchored`. NIBS 2003, Table A.8.6, Table 15B.5.
46 | Pipework Elevated | DS2 Moderate | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.05 | 0.75 | Normal | 1.671 | 0.2 | 2 | HAZUS algorithms for `Eleveted Pipes - Anchored`. NIBS 2003, Table A.8.6, Table 15B.5.
47 | Pipework Elevated | DS3 Extensive | no | Lognormal | 0.53 | 0 | 0.6 | NA | null | null | 0.1 | 0.3 | Normal | 16.7103 | 2 | 20 | HAZUS algorithms for `Eleveted Pipes - Anchored`. NIBS 2003, Table A.8.6, Table 15B.5.
48 | Pipework Elevated | DS4 Complete | no | Lognormal | 1 | 0 | 0.6 | NA | null | null | 0.5 | 0 | Normal | 25.0654 | 3 | 30 | HAZUS algorithms for `Eleveted Pipes - Anchored`. NIBS 2003, Table A.8.6, Table 15B.5.
49 | Backup Genset | DS1 Slight | no | Lognormal | 0.27 | 0 | 0.5 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | GA adaptation of HAZUS algorithm for `Chlorination Equipment`. NIBS 2003, Table A.8.6, Table 15B.5.
50 | Backup Genset | DS2 Moderate | no | Lognormal | 0.35 | 0 | 0.5 | NA | null | null | 0.05 | 0.75 | Normal | 1.671 | 0.2 | 2
51 | Backup Genset | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.5 | 0.3 | Normal | 4.1776 | 0.5 | 5
52 | Backup Genset | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 1 | 0 | Normal | 4.1776 | 0.5 | 5
53 | JUNCTION_NODE | DS1 Slight | no | Lognormal | 101 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 0.41776 | 0.05 | 0.5 | Assigned unbreakable fragiity. | This component is a necessary artefact of of the model.
54 | JUNCTION_NODE | DS2 Moderate | no | Lognormal | 9 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 0.83551 | 0.1 | 1
55 | JUNCTION_NODE | DS3 Extensive | no | Lognormal | 101 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 1.671 | 0.2 | 2
56 | JUNCTION_NODE | DS4 Complete | no | Lognormal | 101 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 3.3421 | 0.4 | 4
57 | Pipe Connector Buried | DS1 Slight | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | Assigned fragility of algorithm for: `Elevated Pipework`
58 | Pipe Connector Buried | DS2 Moderate | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.05 | 0.75 | Normal | 1.671 | 0.2 | 2
59 | Pipe Connector Buried | DS3 Extensive | no | Lognormal | 0.53 | 0 | 0.6 | NA | null | null | 0.1 | 0.3 | Normal | 3.3421 | 0.4 | 4
60 | Pipe Connector Buried | DS4 Complete | no | Lognormal | 1 | 0 | 0.6 | NA | null | null | 0.5 | 0 | Normal | 5.8486 | 0.7 | 7
61 | Pipe Connector Overground | DS1 Slight | no | Lognormal | 0.4 | 0 | 0.6 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1
62 | Pipe Connector Overground | DS2 Moderate | no | Lognormal | 0.67 | 0 | 0.7 | NA | null | null | 0.05 | 0.75 | Normal | 1.671 | 0.2 | 2
63 | Pipe Connector Overground | DS3 Extensive | no | Lognormal | 0.85 | 0 | 0.7 | NA | null | null | 0.1 | 0.3 | Normal | 3.3421 | 0.4 | 4
64 | Pipe Connector Overground | DS4 Complete | no | Lognormal | 1 | 0 | 0.7 | NA | null | null | 0.5 | 0 | Normal | 5.8486 | 0.7 | 7
65 | Pipe Main Inlet | DS1 Slight | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | Assigned fragility & recovery algorithm for: `Elevated Pipework`
66 | Pipe Main Inlet | DS2 Moderate | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.05 | 0.75 | Normal | 1.671 | 0.2 | 2
67 | Pipe Main Inlet | DS3 Extensive | no | Lognormal | 0.53 | 0 | 0.6 | NA | null | null | 0.1 | 0.3 | Normal | 16.7103 | 2 | 20
68 | Pipe Main Inlet | DS4 Complete | no | Lognormal | 1 | 0 | 0.6 | NA | null | null | 0.5 | 0 | Normal | 25.0654 | 3 | 30
69 | Pump Horizontal - HAZUS-A | DS1 Slight | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0 | 0.95 | Normal | 0.41776 | 0.05 | 0.5 | HAZUS algorithm for `Horizontal Pump - Anchored - Pumping Plant Subcomponent`. NIBS 2003, Table A.8.1, Table 15B.5.
70 | Pump Horizontal - HAZUS-A | DS2 Moderate | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0 | 0.75 | Normal | 0.83551 | 0.1 | 1
71 | Pump Horizontal - HAZUS-A | DS3 Extensive | no | Lognormal | 1.6 | 0 | 0.6 | NA | null | null | 0.75 | 0.3 | Normal | 1.671 | 0.2 | 2
72 | Pump Horizontal - HAZUS-A | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0 | 0 | Normal | 3.3421 | 0.4 | 4
73 | Pump Horizontal 1500kW | DS1 Slight | no | Lognormal | 0.13 | 0 | 0.6 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | HAZUS algorithm for `Pumping Station - Small with Unanchored Components`. NIBS 2004, Table 8.6.
74 | Pump Horizontal 1500kW | DS2 Moderate | no | Lognormal | 0.28 | 0 | 0.5 | NA | null | null | 0.05 | 0.75 | Normal | 1.671 | 0.2 | 2
75 | Pump Horizontal 1500kW | DS3 Extensive | no | Lognormal | 0.55 | 0 | 0.5 | NA | null | null | 0.5 | 0.3 | Normal | 4.1776 | 0.5 | 5
76 | Pump Horizontal 1500kW | DS4 Complete | no | Lognormal | 1.05 | 0 | 0.4 | NA | null | null | 1 | 0 | Normal | 8.3551 | 1 | 10
77 | Pump Vertical - HAZUS-A | DS1 Slight | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0 | 0.95 | Normal | 0.41776 | 0.05 | 0.5 | HAZUS algorithm for `Vertical Pump - Anchored - Pumping Plant Subcomponent`. NIBS 2003, Table A.8.1, Table 15B.5.
78 | Pump Vertical - HAZUS-A | DS2 Moderate | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0 | 0.75 | Normal | 0.83551 | 0.1 | 1
79 | Pump Vertical - HAZUS-A | DS3 Extensive | no | Lognormal | 1.25 | 0 | 0.6 | NA | null | null | 0.75 | 0.3 | Normal | 1.671 | 0.2 | 2
80 | Pump Vertical - HAZUS-A | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 1 | 0 | Normal | 3.3421 | 0.4 | 4
81 | RC Tank On Ground - Anchored | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.55 | NA | null | null | 0.01 | 0.95 | Normal | 1.671 | 0.2 | 2 | HAZUS algorithm for Concrete Tank On-ground, Anchored. NIBS 2004, Table 8.9.
82 | RC Tank On Ground - Anchored | DS2 Moderate | no | Lognormal | 0.52 | 0 | 0.7 | NA | null | null | 0.05 | 0.75 | Normal | 25.0654 | 3 | 30 | HAZUS algorithm for Concrete Tank On-ground, Anchored. NIBS 2004, Table 8.9.
83 | RC Tank On Ground - Anchored | DS3 Extensive | no | Lognormal | 0.95 | 0 | 0.6 | NA | null | null | 0.5 | 0.3 | Normal | 167.1029 | 20 | 200 | HAZUS algorithm for Concrete Tank On-ground, Anchored. NIBS 2004, Table 8.9.
84 | RC Tank On Ground - Anchored | DS4 Complete | no | Lognormal | 1.64 | 0 | 0.7 | NA | null | null | 1 | 0 | Normal | 167.1029 | 20 | 200 | HAZUS algorithm for Concrete Tank On-ground, Anchored. NIBS 2004, Table 8.9.
85 | Steel Tank Liquid CO2 - 50pct full | DS1 Slight | no | Lognormal | 0.15 | 0 | 0.5 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | Source not appended
86 | Steel Tank Liquid CO2 - 50pct full | DS2 Moderate | no | Lognormal | 0.294 | 0 | 0.5 | NA | null | null | 0.02 | 0.75 | Normal | 0.83551 | 0.1 | 1
87 | Steel Tank Liquid CO2 - 50pct full | DS3 Extensive | no | Lognormal | 0.763 | 0 | 0.52 | NA | null | null | 0.5 | 0.3 | Normal | 0.83551 | 0.1 | 1
88 | Steel Tank Liquid CO2 - 50pct full | DS4 Complete | no | Lognormal | 1.2 | 0 | 0.6 | NA | null | null | 0.5 | 0 | Normal | 0.83551 | 0.1 | 1
89 | Steel Tank Liquid CO2 - 100pct full | DS1 Slight | no | Lognormal | 0.08 | 0 | 0.5 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | Source not appended
90 | Steel Tank Liquid CO2 - 100pct full | DS2 Moderate | no | Lognormal | 0.163 | 0 | 0.5 | NA | null | null | 0.02 | 0.75 | Normal | 0.83551 | 0.1 | 1
91 | Steel Tank Liquid CO2 - 100pct full | DS3 Extensive | no | Lognormal | 0.424 | 0 | 0.52 | NA | null | null | 0.5 | 0.3 | Normal | 0.83551 | 0.1 | 1
92 | Steel Tank Liquid CO2 - 100pct full | DS4 Complete | no | Lognormal | 0.75 | 0 | 0.7 | NA | null | null | 0.5 | 0 | Normal | 0.83551 | 0.1 | 1
93 | Surge Vessels | DS1 Slight | no | Lognormal | 0.4 | 0 | 0.35 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | Expert Judgment
94 | Surge Vessels | DS2 Moderate | no | Lognormal | 0.45 | 0 | 0.35 | NA | null | null | 0.02 | 0.75 | Normal | 0.83551 | 0.1 | 1
95 | Surge Vessels | DS3 Extensive | no | Lognormal | 0.53 | 0 | 0.38 | NA | null | null | 0.5 | 0.3 | Normal | 1.671 | 0.2 | 2
96 | Surge Vessels | DS4 Complete | no | Lognormal | 0.7 | 0 | 0.45 | NA | null | null | 0.5 | 0 | Normal | 1.671 | 0.2 | 2
97 | Switchrooms | DS1 Slight | no | Lognormal | 0.15 | 0 | 0.4 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | GA adaptation. HAZUS Unanchored algorithm for swtichrooms. Building 0.15 for Extensive and Complete.
98 | Switchrooms | DS2 Moderate | no | Lognormal | 0.3 | 0 | 0.4 | NA | null | null | 0.02 | 0.75 | Normal | 1.671 | 0.2 | 2
99 | Switchrooms | DS3 Extensive | no | Lognormal | 0.55 | 0 | 0.4 | NA | null | null | 0.5 | 0.3 | Normal | 16.7103 | 2 | 20
100 | Switchrooms | DS4 Complete | no | Lognormal | 0.8 | 0 | 0.4 | NA | null | null | 1 | 0 | Normal | 25.0654 | 3 | 30
101 | SYSTEM_INPUT | DS1 Slight | no | Lognormal | 101 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 0.41776 | 0.05 | 0.5 | Assigned unbreakable fragiity. | This component is a necessary artefact of of the model.
102 | SYSTEM_INPUT | DS2 Moderate | no | Lognormal | 101 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 0.83551 | 0.1 | 1
103 | SYSTEM_INPUT | DS3 Extensive | no | Lognormal | 101 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 1.671 | 0.2 | 2
104 | SYSTEM_INPUT | DS4 Complete | no | Lognormal | 101 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 3.3421 | 0.4 | 4
105 | SYSTEM_OUTPUT | DS1 Slight | no | Lognormal | 101 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 0.41776 | 0.05 | 0.5 | Assigned unbreakable fragiity. | This component is a necessary artefact of of the model.
106 | SYSTEM_OUTPUT | DS2 Moderate | no | Lognormal | 101 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 0.83551 | 0.1 | 1
107 | SYSTEM_OUTPUT | DS3 Extensive | no | Lognormal | 101 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 1.671 | 0.2 | 2
108 | SYSTEM_OUTPUT | DS4 Complete | no | Lognormal | 101 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 3.3421 | 0.4 | 4
109 | Transformer | DS1 Slight | no | Lognormal | 0.1 | 0 | 0.5 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | EPN14 115/12KV | Slight and moderate as per diesel tank. EPN14 for sliding failure but moved 0.1g to right (very similar to diesel tank). EPN14 for overturning.
110 | Transformer | DS2 Moderate | no | Lognormal | 0.21 | 0 | 0.5 | NA | null | null | 0.1 | 0.75 | Normal | 1.671 | 0.2 | 2
111 | Transformer | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 1 | 0.3 | Normal | 8.3551 | 1 | 10
112 | Transformer | DS4 Complete | no | Lognormal | 0.8 | 0 | 0.39 | NA | null | null | 1 | 0 | Normal | 8.3551 | 1 | 10
113 | Transformer Dry Type | DS1 Slight | no | Lognormal | 0.1 | 0 | 0.5 | NA | null | null | 0.01 | 0.95 | Normal | 0.83551 | 0.1 | 1 | Adapted from EPN14 115/12KV
114 | Transformer Dry Type | DS2 Moderate | no | Lognormal | 0.21 | 0 | 0.5 | NA | null | null | 0.1 | 0.75 | Normal | 1.671 | 0.2 | 2
115 | Transformer Dry Type | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 1 | 0.3 | Normal | 1.671 | 0.2 | 2
116 | Transformer Dry Type | DS4 Complete | no | Lognormal | 0.48 | 0 | 0.39 | NA | null | null | 1 | 0 | Normal | 4.1776 | 0.5 | 5
117 | Transformer Kiosk | DS1 Slight | no | Lognormal | 0.14 | 0 | 0.5 | NA | null | null | 0.05 | 0.95 | Normal | 0.83551 | 0.1 | 1 | Assigned fragility of algorithm for: `Transformer`.
118 | Transformer Kiosk | DS2 Moderate | no | Lognormal | 0.27 | 0 | 0.5 | NA | null | null | 0.1 | 0.75 | Normal | 1.671 | 0.2 | 2
119 | Transformer Kiosk | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.8 | 0.3 | Normal | 8.3551 | 1 | 10
120 | Transformer Kiosk | DS4 Complete | no | Lognormal | 0.8 | 0 | 0.39 | NA | null | null | 1 | 0 | Normal | 8.3551 | 1 | 10

## damage_state_def
component_type | damage_state | damage_state_definition
Electric Power Commercial | DS1 Slight | Power source to model. Assumed seismically invulnerable for simulation purposes.
Electric Power Commercial | DS2 Moderate | Power source to model. Assumed seismically invulnerable for simulation purposes.
Electric Power Commercial | DS3 Extensive | Power source to model. Assumed seismically invulnerable for simulation purposes.
Electric Power Commercial | DS4 Complete | Power source to model. Assumed seismically invulnerable for simulation purposes.
SYSTEM_INPUT | DS1 Slight | Model artefact. Assumed seismically invulnerable for simulation purposes.
SYSTEM_INPUT | DS2 Moderate | Model artefact. Assumed seismically invulnerable for simulation purposes.
SYSTEM_INPUT | DS3 Extensive | Model artefact. Assumed seismically invulnerable for simulation purposes.
SYSTEM_INPUT | DS4 Complete | Model artefact. Assumed seismically invulnerable for simulation purposes.
SYSTEM_OUTPUT | DS1 Slight | Model artefact. Assumed seismically invulnerable for simulation purposes.
SYSTEM_OUTPUT | DS2 Moderate | Model artefact. Assumed seismically invulnerable for simulation purposes.
SYSTEM_OUTPUT | DS3 Extensive | Model artefact. Assumed seismically invulnerable for simulation purposes.
SYSTEM_OUTPUT | DS4 Complete | Model artefact. Assumed seismically invulnerable for simulation purposes.
JUNCTION | DS1 Slight | Model artefact. Assumed seismically invulnerable for simulation purposes.
JUNCTION | DS2 Moderate | Model artefact. Assumed seismically invulnerable for simulation purposes.
JUNCTION | DS3 Extensive | Model artefact. Assumed seismically invulnerable for simulation purposes.
JUNCTION | DS4 Complete | Model artefact. Assumed seismically invulnerable for simulation purposes.
Air Tank Vertical | DS1 Slight | Minor base movement with yield of HD bolts
Air Tank Vertical | DS2 Moderate | Some elongation of HD bolts with yieldng of support legs
Air Tank Vertical | DS3 Extensive | Yielding of HD bolts and failure of legs causing overturning but checked by building structure (25% as likely as full overturning)
Air Tank Vertical | DS4 Complete | Complete overturning
Building Tilt-up Concrete | DS1 Slight | Minor damage to cladding and doors due to building sway.
Building Tilt-up Concrete | DS2 Moderate | Some yielding of bolts in moment connections of steel portal frames. Yielding around bolting of diagonal bracing connections and braced member resulting in slack. Cladding and doors more extensively damaged. Some damage to precast wall panel connections where present.
Building Tilt-up Concrete | DS3 Extensive | Extensive yielding of bolts in moment connections of steel portal frames with permanent drift. Some tension failures of diagonal bracing end connections and significant slack in non-failed bracing. Cladding and doors more extensively damaged due to significant permanent drift in the building. Precast panel damage more extensive.
Building Tilt-up Concrete | DS4 Complete | Building has numerous failures in structural system and extensive drift to the point of collapse.
Chemical Building | DS1 Slight | Minor damage to cladding and doors due to building sway.
Chemical Building | DS2 Moderate | Some yielding of bolts in moment connections of steel portal frames. Yielding around bolting of diagonal bracing connections and braced member resulting in slack. Cladding and doors more extensively damaged. Some damage to precast wall panel connections where present.
Chemical Building | DS3 Extensive | Extensive yielding of bolts in moment connections of steel portal frames with permanent drift. Some tension failures of diagonal bracing end connections and significant slack in non-failed bracing. Cladding and doors more extensively damaged. Precast panel damage more extensive.
Chemical Building | DS4 Complete | Building has numerous failures in structural system and extensive drift to the point of collapse.
Chemical Dosing Panel | DS1 Slight | Partial overturning without equipment damage in panel
Chemical Dosing Panel | DS2 Moderate | Overturning with damage to dosing equipment components
Chemical Dosing Panel | DS3 Extensive | Panel suffering extensive damage due to partial building failure crushing panel
Chemical Dosing Panel | DS4 Complete | Panel destroyed due to building collapse
Chemical Tanks PE | DS1 Slight | Significant tank movement on pedestal
Chemical Tanks PE | DS2 Moderate | Major tank movement on pedestal. Damage to HDPE at HD bolt.
Chemical Tanks PE | DS3 Extensive | Extensive tearing and tank movement
Chemical Tanks PE | DS4 Complete | Ruptured tank
Chlorination Equipment | DS1 Slight | Minor damage to connections and pipework
Chlorination Equipment | DS2 Moderate | Yielding of connection plates, metering equipment and damage to pipework. Some leakage of chemical solutions.
Chlorination Equipment | DS3 Extensive | Extensive damage to metering equipment and pipework with yielding of support brackets and connections
Chlorination Equipment | DS4 Complete | Severe damage to metering equipment and pipework with extensive yielding of support brackets and connections and permanent drift of assembly
Compressed Air Vessel | DS1 Slight | Minor base movement with yield of HD bolts
Compressed Air Vessel | DS2 Moderate | Some elongation of HD bolts with yielding of support legs laterally
Compressed Air Vessel | DS3 Extensive | Yielding of HD bolts and failure of legs causing overturning but checked by building structure (25% as likely as full overturning)
Compressed Air Vessel | DS4 Complete | Complete overturning
RC Tank On Ground - Anchored | DS1 Slight | Minor cracking of concrete tank walls. No leakage. Minor damage to steel clad steel roof structures
RC Tank On Ground - Anchored | DS2 Moderate | Moderate cracking of tank wall with some leakage. Roof damage more extensive at support structure connection to tanks walls and to cladding due to the effects of sloshing within the tank.
RC Tank On Ground - Anchored | DS3 Extensive | Extensive cracking with yielding of reinforcement and permanent deformation. Concrete tank leakage renders tank unusable. Roof structure compromised by failure of support connections to tank walls.
RC Tank On Ground - Anchored | DS4 Complete | Severe damage to tanks wall with wide cracking, damage to construction joints and permanent deformation of the walls. Roof structure where present may suffer partial collapse. Some tanks may experience complete collapse of wall with loss of contents.
Diesel Storage Tank Horizontal | DS1 Slight | Minor base movement.
Diesel Storage Tank Horizontal | DS2 Moderate | Extensive movement without overturning but with damage to diesel pipework.
Diesel Storage Tank Horizontal | DS3 Extensive | Wall buckling of tank due to sloshing of fuel
Diesel Storage Tank Horizontal | DS4 Complete | NA
Elevated Pipework | DS1 Slight | Minor damage to supporting structure and pipework
Elevated Pipework | DS2 Moderate | Yielding of HD bolts and minor yielding of steel members supporting pipework. Some permanent deformation of pipework.
Elevated Pipework | DS3 Extensive | Extensive damage to support structures with permanent drift and misalignment. Pipework sustains yielding and leakage, particularly at interfaces with stiffer equipment at building faces.
Elevated Pipework | DS4 Complete | Severe damage with overturning of some support structures. Pipework is damaged with several leaks and some breaks at connections. Steel support structure deformed with failure of some connections.
Electrical Kiosk Switchroom | DS1 Slight | Minor joint movement between precast panels. Minor yielding of welded inter-panel connections and roof plane bracing elements. Some movement of switchgear panels
Electrical Kiosk Switchroom | DS2 Moderate | Significant movement at panel joints with damage of mastic sealant. Yielding around bolting of diagonal bracing connections and braced members resulting in slack. Cladding and doors damaged. Some damage to precast wall panel connections due to yielding at connections. Unrestrained equipment moves with some cable damage below.
Electrical Kiosk Switchroom | DS3 Extensive | Extensive yielding of bolts and brace end connections. Some tension failures of diagonal bracing end connections and significant slack in non-failed bracing. Cladding and doors more extensively damaged. Precast panel damage at connections more extensive with some failures at welds. Some overturning of switch gear panels and UPS equipment.
Electrical Kiosk Switchroom | DS4 Complete | Building has numerous failures in structural system with extensive drift and detachment of some precast panels. Equipment extensively damaged.
Electrical Kiosk Transformer | DS1 Slight | Minor base movement.
Electrical Kiosk Transformer | DS2 Moderate | Extensive sliding damage to cables of transformer.
Electrical Kiosk Transformer | DS3 Extensive | Extensive sliding damage to cables of transformer with internal transformer damage.
Electrical Kiosk Transformer | DS4 Complete | Overturning.
Transformer Kiosk Oil-Filled | DS1 Slight | Minor base movement.
Transformer Kiosk Oil-Filled | DS2 Moderate | Extensive sliding damage to cables of transformer.
Transformer Kiosk Oil-Filled | DS3 Extensive | Extensive sliding damage to cables of transformer with internal transformer damage.
Transformer Kiosk Oil-Filled | DS4 Complete | Overturning.
Backup Genset | DS1 Slight | Minor base movement.
Backup Genset | DS2 Moderate | Extensive movement without overturning with damage to fuel supply pipework and cabling.
Backup Genset | DS3 Extensive | Extensive movement without overturning/ Rupture of diesel fuel lines and extensive cable damage. Digital motor failure with stepping.
Backup Genset | DS4 Complete | Overturning of assembly with extensive damage to motor, generator and switchgear.
Switchrooms | DS1 Slight | Minor joint movement between precast panels. Minor yielding of welded inter-panel connections and roof plane bracing elements. Some movement of switchgear panels
Switchrooms | DS2 Moderate | Significant movement at panel joints with damage to mastic sealant. Yielding around bolting of diagonal bracing connections and braced members resulting in slack. Cladding and doors damaged. Some damage to precast wall panel connections due to yielding at connections. Unrestrained equipment moves with some cable damage below.
Switchrooms | DS3 Extensive | Extensive yielding of bolts and brace end connections. Some tension failures of diagonal bracing end connections and significant slack in non-failed bracing. Cladding and doors more extensively damaged. Precast panel damage at connections more extensive with some failures at welds. Some overturning of switch gear panels and UPS equipment.
Switchrooms | DS4 Complete | Building has numerous failures in structural system with extensive drift and detachment of some precast panels. Equipment extensively damaged.
Transformer | DS1 Slight | Minor base movement.
Transformer | DS2 Moderate | Extensive sliding damage to cables of transformer.
Transformer | DS3 Extensive | Extensive sliding damage to cables of transformer, with internal transformer damage.
Transformer | DS4 Complete | Overturning.
Transformer Dry Type | DS1 Slight | Minor base movement.
Transformer Dry Type | DS2 Moderate | Extensive sliding damage to cables beneath transformer.
Transformer Dry Type | DS3 Extensive | NA
Transformer Dry Type | DS4 Complete | Internal overturning of air cooled core.
Steel Tank Liquid CO2 | DS1 Slight | Minor base movement with yield of HD bolts.
Steel Tank Liquid CO2 | DS2 Moderate | Moderate to major elongation of HD bolts.
Steel Tank Liquid CO2 | DS3 Extensive | Extensive overturning but checked by chemical buildings (25% as likely as full overturning). Connecting pipework extensively damaged.
Steel Tank Liquid CO2 | DS4 Complete | Complete overturning with rupture of connecting pipework.
Surge Vessels | DS1 Slight | Minor base movement with yield of HD bolts
Surge Vessels | DS2 Moderate | Major elongation of HD bolts
Surge Vessels | DS3 Extensive | Damage to base support with significant permanent drift in the vessel
Surge Vessels | DS4 Complete | Complete overturning
Pipe Connector Buried | DS1 Slight
Pipe Connector Buried | DS2 Moderate
Pipe Connector Buried | DS3 Extensive
Pipe Connector Buried | DS4 Complete
Pipe Connector Overground | DS1 Slight
Pipe Connector Overground | DS2 Moderate
Pipe Connector Overground | DS3 Extensive
Pipe Connector Overground | DS4 Complete
Pipe Joint | DS1 Slight | Leakage
Pipe Joint | DS2 Moderate | Break
Pipe Joint | DS3 Extensive | NA
Pipe Joint | DS4 Complete | NA
Pipe Main Inlet | DS1 Slight
Pipe Main Inlet | DS2 Moderate
Pipe Main Inlet | DS3 Extensive
Pipe Main Inlet | DS4 Complete
Pipe Section DN1200 | DS1 Slight
Pipe Section DN1200 | DS2 Moderate
Pipe Section DN1200 | DS3 Extensive
Pipe Section DN1200 | DS4 Complete
Pipe Section DN1400 | DS1 Slight
Pipe Section DN1400 | DS2 Moderate
Pipe Section DN1400 | DS3 Extensive
Pipe Section DN1400 | DS4 Complete
Pump Horizontal 1600kW | DS1 Slight | Minor damage and movement of pump equipment with some yielding of holding down bolting and pipe support structure.
Pump Horizontal 1600kW | DS2 Moderate | Damage to holding down bolting, support steel sledge and supporting steel pedestals to pipework. Some damage to pipework flanged and pipe wall with permanent deformation of pipe wall.
Pump Horizontal 1600kW | DS3 Extensive | Extensive damage to pumps, drive motors and associated pipework due to horizontal movement. Holding down bolting sheared in some instances. Some shaft damage to pump and motor.
Pump Horizontal 1600kW | DS4 Complete | Irreparable damage to the pumps and motors due to horizontal movement with equipment displaced from the pedestals. Connecting pipework extensively damaged.
Pump Backwash | DS1 Slight | Minor damage and movement of pump equipment with some yielding of holding down bolting and pipe support structure. | Malfunction of plant for a short time (<3 days) due to electric power loss or slight building damage. [SRM-LIFE (2007)]
Pump Backwash | DS2 Moderate | Damage to holding down bolting, support steel sledge and pipework. Some permanent deformation of pipe wall particularly at connections. | Loss of electric power for about a week, considerable damage to mechanical and electrical equipment, or moderate building damage. [SRM-LIFE (2007)]
Pump Backwash | DS3 Extensive | Extensive damage to pumps, drive motors and associated pipework due to horizontal movement. Holding down bolting significantly deformed in some instances. Some shaft damage to pump and motor. | Extensive building damage or extensive, beyond repair, pump damage. [SRM-LIFE (2007)]
Pump Backwash | DS4 Complete | Irreparable damage to the pumps and motors due to horizontal movement with equipment displaced from the pedestals. Connecting pipework extensively damaged. | Building collapse. [SRM-LIFE (2007)]
UV Dosing Equipment | DS1 Slight | Minor damage to supporting structure and pipework
UV Dosing Equipment | DS2 Moderate | Yielding of HD bolts and minor yielding of steel members supporting UV equipment. Some permanent deformation in pipework.
UV Dosing Equipment | DS3 Extensive | Extensive damage to UV equipment support with permanent drift and misalignment. Pipework sustains yielding and damage.
UV Dosing Equipment | DS4 Complete | Severe damage with overturning of UV units with damage to power supply and connecting pipework. Steel support structure deformed with failure of some connections and significant permanent drift.
Basins | DS1 Slight
Basins | DS2 Moderate
Basins | DS3 Extensive
Basins | DS4 Complete
Pump Horizontal - HAZUS-A | DS1 Slight
Pump Horizontal - HAZUS-A | DS2 Moderate
Pump Horizontal - HAZUS-A | DS3 Extensive
Pump Horizontal - HAZUS-A | DS4 Complete
Pump Vertical - HAZUS-A | DS1 Slight
Pump Vertical - HAZUS-A | DS2 Moderate
Pump Vertical - HAZUS-A | DS3 Extensive
Pump Vertical - HAZUS-A | DS4 Complete

## VALIDATION_TABLES
INFRASTRUCTURE_LEVEL | SYSTEM_CLASSES | RESTORATION_TIME_UNIT | COMPONENT_LOCATION_CONF
facility | PowerStation | days | defined
network | Substation | weeks | undefined
| PotableWaterTreatmentPlant | months | schematic
| PWTP | years | geospatial
WasteWaterTreatmentPlant
WWTP
PotableWaterPumpStation
ElectricPowerNetwork
PotableWaterNetwork
RailNetwork

## asset_names
Component Types | Synonyms | Note
Baffles
Basins
Building Tilt-up Concrete
Chemical Building
Chemical Dosing Panel
Chemical Tanks PE | Chemical Tank - fibreglass reinforced polyethylene
Chlorination Equipment | Chlorination Equipment - Chlorine
Chlorine Storage Building
Circular Clarification Tank
Compressed Air Vessel
Concrete Tank 10x10 | Thickened Sludge Tank & Pumps
Concrete Tank 10X20 BACRINSE | BAC Rinse & Supernatant Tank
Concrete Tank 20x20 BKWSH | Backwash Water Storage Tank
Concrete Tank 20x20 CLCONTACT | Chlorine Contact Tank
Concrete Tank 20x25 FLOC | Flocculation Tanks
Concrete Tank 20x25 WASHWATER | Washwater Tank & Recovery Pumps
Concrete Tank 20x80 BACFILTER | BAC Filters
Concrete Tank 30x30 CLRWTR | Clearwater Storage Tank No.1
Concrete Tank 30x70 DAFF | DAFF Tanks
Concrete Tank BALANCING | Balancing Tank
Diesel Storage Tank Horizontal
Electric Power Supply Backup
Electric Power Supply Commercial
Electric Switchboard
Electric Control Panel
Electrical HV Switchroom
Electrical HV-LV Switchroom
Electrical Kiosk Switchroom
Flow Equalisation Basin
Genset 3100kVA
Grit Chamber
JUNCTION
Paddles
Pipe Connector Buried
Pipe Connector Overground
Pipe Connector Suspended
Pipe Joint
Pipe Main Inlet
Pipe Section DN1200
Pipe Section DN1400
Pipe Section DN1700
Pipework Elevated
Pipework Internal
Primary Clarifier Tank
Pump Backwash
Pump Horizontal - HAZUS-A
Pump Vertical - HAZUS-A
Pump Horizontal 1600kW
Pump Station
RC Tank On Ground - Anchored
Rectangular Sedimentation Tank
Reservoir
Scrapers
Secondary Treatment Tank
Sediment Flocculation
Sludge Digesters
Steel Tank Liquid CO2
Steel Tank Liquid CO2 - 50pct full
Steel Tank Liquid CO2 - 100pct full
Step Screens
Supernatant Pump Filter
SUPPLY_NODES
Surge Vessels
Switchrooms
SYSTEM_INPUT
SYSTEM_OUTPUT
Transformer
Transformer Kiosk
Transformer Dry Type
Transformer Kiosk Oil-Filled
UV Dosing Equipment | Dosing Equipment - UV
Air Tank Vertical
Voltage Transformer
Wells