## system_meta
model_config_param | value | notes
MODEL_NAME | Substation 66-22kV
INFRASTRUCTURE_LEVEL | facility
SYSTEM_CLASS | Substation
SYSTEM_SUBCLASS | Transmission Substation
SYSTEM_COMPONENT_LOCATION_CONF | defined
RESTORATION_TIME_UNIT | days
HAZARD_INTENSITY_MEASURE_PARAM | PGA
HAZARD_INTENSITY_MEASURE_UNIT | g

## table_description
Table Name | Description | Note
component_list | This table lists the components constituting the Northern Terminal substation in Malaga, WA. Assumed component design level x.xx g. | Cost fraction is a normalised value of components in the system. It defines economic value of individual components relative to the cost of the entire system. Data includes a __% allowance for components not included in the model.
component_connections | Network connections. Each pair of nodes implies a connecting edge. Directionality is defined by order of nodes in a row (Orig -> Dest). | Used by: (1) network algorithm package for flow calculations, (2) Pygraphviz to draw the system layout.
supply_setup | Necessary input materiél required for plant operation. | Capacity given as percentage.
output_setup | Output capacity measured in MW.
comp_type_dmg_algo | List of component types with fragility and recovery data | Fragilities are defined according to discrete damage states. Recovery time is in DAYS.
damage_state_def | Definitions of damage states of the list of component types in the system

## component_list
component_id | component_type | component_class | cost_fraction | node_type | node_cluster | operating_capacity | pos_x | pos_y | site_id
CTRL_BLDG | Building Timber Framed Pre War | Control Building | 0.028121 | dependency | BAY_CTRL_A | 1 | 1825 | 150 | 6
CTRL_EQP_BATTERY | Battery Racks Unbraced | Station Power Supply | 0.0056243 | transshipment | BAY_CTRL_B | 1 | 1650 | 150 | 6
CTRL_EQP | Switchgear Low Voltage Legacy | Station Power Supply | 0.033746 | transshipment | BAY_CTRL_C | 1 | 1825 | 275 | 6
CTRL_LINES_JNC1 | JUNCTION_NODE | MODEL ARTEFACT | 0 | junction | BAY_CTRL_J | 1 | 1825 | 2770 | 6
TX_STN22 | Station Transformer 66kV 22kV Unrestrained | Station Power Supply | 0.067492 | transshipment | BAY_RTX101 | 1 | 100 | 920 | 6
LINE_X02 | SYSTEM_OUTPUT | MODEL ARTEFACT | 0 | sink | BAY_RTX102A | 1 | 275 | 460 | 6
BUS_RTX22_SEC-A | Bus 22 66 Legacy | Bus | 0.011811 | transshipment | BAY_RTX102B | 1 | 275 | 580 | 6
DS_RTX102_5 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.0067492 | transshipment | BAY_RTX102C | 1 | 275 | 700 | 6
CT_RTX102 | Current Transformer 22 66kV Legacy | Current Transformer | 0.007874 | transshipment | BAY_RTX102D | 1 | 275 | 800 | 6
CB_RTX102_0 | Circuit Breaker Live Tank 66kV 22kV Legacy | Circuit Breaker | 0.007874 | transshipment | BAY_RTX102E | 1 | 275 | 920 | 6
DS_RTX102_4 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.0067492 | transshipment | BAY_RTX102F | 1 | 275 | 1040 | 6
DS_RTX103_8 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.0067492 | transshipment | BAY_RTX103_0 | 1 | 450 | 580 | 6
LINE_X03 | SYSTEM_OUTPUT | MODEL ARTEFACT | 0 | sink | BAY_RTX103A | 1 | 625 | 460 | 6
BUS_RTX22_SEC-B | Bus 22 66 Legacy | Bus | 0.011811 | transshipment | BAY_RTX103B | 1 | 625 | 580 | 6
DS_RTX103_5 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.0067492 | transshipment | BAY_RTX103C | 1 | 625 | 700 | 6
CT_RTX103 | Current Transformer 22 66kV Legacy | Current Transformer | 0.007874 | transshipment | BAY_RTX103D | 1 | 625 | 800 | 6
CB_RTX103_0 | Circuit Breaker Live Tank 66kV 22kV Legacy | Circuit Breaker | 0.007874 | transshipment | BAY_RTX103E | 1 | 625 | 920 | 6
DS_RTX103_4 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.0067492 | transshipment | BAY_RTX103F | 1 | 625 | 1040 | 6
BUS_RTX22_PRI-A | Bus 22 66 Legacy | Bus | 0.015748 | transshipment | BAY_RTX104-702A | 1 | 800 | 1160 | 6
DS_RTX104_4 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.0067492 | transshipment | BAY_RTX104-702B | 1 | 800 | 1280 | 6
VT_RTX104 | Voltage Transformer 22 66kV Legacy | Voltage Transformer | 0.0089989 | transshipment | BAY_RTX104-702C | 1 | 800 | 1380 | 6
PTX_66-22KV_T3 | Transformer 22 66kV Unestrained | Power Transformer | 0.16873 | transshipment | BAY_RTX104-702D | 1 | 800 | 1580 | 6
LA_RTX202 | Lightning Arrestor | Surge Protection | 0.007874 | transshipment | BAY_RTX104-702E | 1 | 800 | 1700 | 6
DS_RTX202_4 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.010124 | transshipment | BAY_RTX104-702F | 1 | 800 | 1820 | 6
BUS_RTX66_A | Bus 22 66 Legacy | Bus | 0.038245 | transshipment | BAY_RTX104-702G | 1 | 800 | 1940 | 6
DS_RTX105_8 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.0067492 | transshipment | BAY_RTX105_0 | 1 | 800 | 580 | 6
LINE_X05 | SYSTEM_OUTPUT | MODEL ARTEFACT | 0 | sink | BAY_RTX105A | 1 | 975 | 460 | 6
BUS_RTX22_SEC-C | Bus 22 66 Legacy | Bus | 0.011811 | transshipment | BAY_RTX105B | 1 | 975 | 580 | 6
DS_RTX105_5 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.0067492 | transshipment | BAY_RTX105C | 1 | 975 | 700 | 6
CT_RTX105 | Current Transformer 22 66kV Legacy | Current Transformer | 0.007874 | transshipment | BAY_RTX105D | 1 | 975 | 800 | 6
CB_RTX105_0 | Circuit Breaker Live Tank 66kV 22kV Legacy | Circuit Breaker | 0.007874 | transshipment | BAY_RTX105E | 1 | 975 | 920 | 6
DS_RTX105_4 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.0067492 | transshipment | BAY_RTX105F | 1 | 975 | 1040 | 6
DS_RTX106_4 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.0067492 | transshipment | BAY_RTX106_0 | 1 | 1150 | 1160 | 6
DS_RTX108_8 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.0067492 | transshipment | BAY_RTX108_0 | 1 | 1150 | 580 | 6
LINE_X08 | SYSTEM_OUTPUT | MODEL ARTEFACT | 0 | sink | BAY_RTX108A | 1 | 1325 | 460 | 6
BUS_RTX22_SEC-D | Bus 22 66 Legacy | Bus | 0.011811 | transshipment | BAY_RTX108B | 1 | 1325 | 580 | 6
DS_RTX108_5 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.0067492 | transshipment | BAY_RTX108C | 1 | 1325 | 700 | 6
CT_RTX108 | Current Transformer 22 66kV Legacy | Current Transformer | 0.007874 | transshipment | BAY_RTX108D | 1 | 1325 | 800 | 6
CB_RTX108_0 | Circuit Breaker Live Tank 66kV 22kV Legacy | Circuit Breaker | 0.007874 | transshipment | BAY_RTX108E | 1 | 1325 | 920 | 6
DS_RTX108_4 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.0067492 | transshipment | BAY_RTX108F | 1 | 1325 | 1040 | 6
BUS_RTX22_PRI-B | Bus 22 66 Legacy | Bus | 0.015748 | transshipment | BAY_RTX108G | 1 | 1325 | 1160 | 6
DS_RTX109_4 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.0067492 | transshipment | BAY_RTX109 | 1 | 1500 | 1160 | 6
BUS_RTX22_PRI-C | Bus 22 66 Legacy | Bus | 0.015748 | transshipment | BAY_RTX110-707A | 1 | 1650 | 1160 | 6
DS_RTX110_4 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.0067492 | transshipment | BAY_RTX110-707B | 1 | 1650 | 1280 | 6
VT_RTX110 | Voltage Transformer 22 66kV Legacy | Voltage Transformer | 0.0089989 | transshipment | BAY_RTX110-707C | 1 | 1650 | 1380 | 6
PTX_66-22KV_T1 | Transformer 22 66kV Unestrained | Power Transformer | 0.16873 | transshipment | BAY_RTX110-707D | 1 | 1650 | 1580 | 6
LA_RTX207 | Lightning Arrestor | Surge Protection | 0.007874 | transshipment | BAY_RTX110-707E | 1 | 1650 | 1700 | 6
DS_RTX207_4 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.010124 | transshipment | BAY_RTX110-707F | 1 | 1650 | 1820 | 6
DS_RTX201_4 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.010124 | transshipment | BAY_RTX201A | 1 | 775 | 2060 | 6
CB_RTX201_0 | Circuit Breaker Live Tank 66kV 22kV Legacy | Circuit Breaker | 0.011249 | transshipment | BAY_RTX201B | 1 | 775 | 2180 | 6
DS_RTX201_5 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.010124 | transshipment | BAY_RTX201C | 1 | 775 | 2300 | 6
VT_RTX201 | Voltage Transformer 22 66kV Legacy | Voltage Transformer | 0.0089989 | transshipment | BAY_RTX201D | 1 | 775 | 2400 | 6
LINE_SSM-SSB-17 | SYSTEM_OUTPUT | MODEL ARTEFACT | 0 | sink | BAY_RTX201E | 1 | 775 | 2570 | 6
DS_RTX203_4 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.010124 | transshipment | BAY_RTX203 | 1 | 975 | 1940 | 6
BUS_RTX66_B | Bus 22 66 Legacy | Bus | 0.03712 | transshipment | BAY_RTX204 | 1 | 1225 | 1940 | 6
DS_RTX205_4 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.010124 | transshipment | BAY_RTX205 | 1 | 1437 | 1940 | 6
LINE_SSC-17 | SYSTEM_INPUT | MODEL ARTEFACT | 0 | supply | BAY_RTX206 | 1 | 1575 | 2570 | 6
BUS_RTX66_C | Bus 22 66 Legacy | Bus | 0.038245 | transshipment | BAY_RTX206A | 1 | 1650 | 1940 | 6
DS_RTX206_4 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.010124 | transshipment | BAY_RTX206B | 1 | 1575 | 2060 | 6
CB_RTX206_0 | Circuit Breaker Live Tank 66kV 22kV Legacy | Circuit Breaker | 0.011249 | transshipment | BAY_RTX206C | 1 | 1575 | 2180 | 6
DS_RTX206_5 | Disconnection Switches 22 66kV Legacy | Disconnect Switch | 0.010124 | transshipment | BAY_RTX206D | 1 | 1575 | 2300 | 6
VT_RTX206 | Voltage Transformer 22 66kV Legacy | Voltage Transformer | 0.0089989 | transshipment | BAY_RTX206E | 1 | 1575 | 2400 | 6

## component_connections
origin | destination | link_capacity | weight
PTX_66-22KV_T3 | VT_RTX104 | 1 | 1
VT_RTX104 | DS_RTX104_4 | 1 | 1
DS_RTX104_4 | BUS_RTX22_PRI-A | 1 | 1
PTX_66-22KV_T1 | VT_RTX110 | 1 | 1
VT_RTX110 | DS_RTX110_4 | 1 | 1
DS_RTX110_4 | BUS_RTX22_PRI-C | 1 | 1
BUS_RTX22_PRI-A | DS_RTX106_4 | 1 | 1
DS_RTX106_4 | BUS_RTX22_PRI-B | 1 | 1
BUS_RTX22_PRI-B | DS_RTX109_4 | 1 | 1
DS_RTX109_4 | BUS_RTX22_PRI-C | 1 | 1
BUS_RTX22_PRI-C | DS_RTX109_4 | 1 | 1
DS_RTX109_4 | BUS_RTX22_PRI-B | 1 | 1
BUS_RTX22_PRI-B | DS_RTX106_4 | 1 | 1
DS_RTX106_4 | BUS_RTX22_PRI-A | 1 | 1
BUS_RTX22_PRI-A | TX_STN22 | 1 | 1
BUS_RTX22_PRI-A | DS_RTX102_4 | 1 | 1
DS_RTX102_4 | CB_RTX102_0 | 1 | 1
CB_RTX102_0 | CT_RTX102 | 1 | 1
CT_RTX102 | DS_RTX102_5 | 1 | 1
DS_RTX102_5 | BUS_RTX22_SEC-A | 1 | 1
BUS_RTX22_SEC-A | LINE_X02 | 1 | 1
BUS_RTX22_PRI-A | DS_RTX103_4 | 1 | 1
DS_RTX103_4 | CB_RTX103_0 | 1 | 1
CB_RTX103_0 | CT_RTX103 | 1 | 1
CT_RTX103 | DS_RTX103_5 | 1 | 1
DS_RTX103_5 | BUS_RTX22_SEC-B | 1 | 1
BUS_RTX22_SEC-B | LINE_X03 | 1 | 1
BUS_RTX22_PRI-A | DS_RTX105_4 | 1 | 1
DS_RTX105_4 | CB_RTX105_0 | 1 | 1
CB_RTX105_0 | CT_RTX105 | 1 | 1
CT_RTX105 | DS_RTX105_5 | 1 | 1
DS_RTX105_5 | BUS_RTX22_SEC-C | 1 | 1
BUS_RTX22_SEC-C | LINE_X05 | 1 | 1
BUS_RTX22_PRI-B | DS_RTX108_4 | 1 | 1
DS_RTX108_4 | CB_RTX108_0 | 1 | 1
CB_RTX108_0 | CT_RTX108 | 1 | 1
CT_RTX108 | DS_RTX108_5 | 1 | 1
DS_RTX108_5 | BUS_RTX22_SEC-D | 1 | 1
BUS_RTX22_SEC-D | LINE_X08 | 1 | 1
BUS_RTX22_SEC-A | DS_RTX103_8 | 1 | 1
DS_RTX103_8 | BUS_RTX22_SEC-B | 1 | 1
BUS_RTX22_SEC-B | DS_RTX103_8 | 1 | 1
DS_RTX103_8 | BUS_RTX22_SEC-A | 1 | 1
BUS_RTX22_SEC-B | DS_RTX105_8 | 1 | 1
DS_RTX105_8 | BUS_RTX22_SEC-C | 1 | 1
BUS_RTX22_SEC-C | DS_RTX105_8 | 1 | 1
DS_RTX105_8 | BUS_RTX22_SEC-B | 1 | 1
BUS_RTX22_SEC-C | DS_RTX108_8 | 1 | 1
DS_RTX108_8 | BUS_RTX22_SEC-D | 1 | 1
BUS_RTX22_SEC-D | DS_RTX108_8 | 1 | 1
DS_RTX108_8 | BUS_RTX22_SEC-C | 1 | 1
LINE_SSC-17 | VT_RTX206 | 1 | 1
VT_RTX206 | DS_RTX206_5 | 1 | 1
DS_RTX206_5 | CB_RTX206_0 | 1 | 1
CB_RTX206_0 | DS_RTX206_4 | 1 | 1
DS_RTX206_4 | BUS_RTX66_C | 1 | 1
BUS_RTX66_C | DS_RTX207_4 | 1 | 1
DS_RTX207_4 | LA_RTX207 | 1 | 1
LA_RTX207 | PTX_66-22KV_T1 | 1 | 1
BUS_RTX66_C | DS_RTX205_4 | 1 | 1
DS_RTX205_4 | BUS_RTX66_B | 1 | 1
BUS_RTX66_B | DS_RTX205_4 | 1 | 1
DS_RTX205_4 | BUS_RTX66_C | 1 | 1
BUS_RTX66_B | DS_RTX203_4 | 1 | 1
DS_RTX203_4 | BUS_RTX66_A | 1 | 1
BUS_RTX66_A | DS_RTX203_4 | 1 | 1
DS_RTX203_4 | BUS_RTX66_B | 1 | 1
BUS_RTX66_A | DS_RTX202_4 | 1 | 1
DS_RTX202_4 | LA_RTX202 | 1 | 1
LA_RTX202 | PTX_66-22KV_T3 | 1 | 1
BUS_RTX66_A | DS_RTX201_4 | 1 | 1
DS_RTX201_4 | CB_RTX201_0 | 1 | 1
CB_RTX201_0 | DS_RTX201_5 | 1 | 1
DS_RTX201_5 | VT_RTX201 | 1 | 1
VT_RTX201 | LINE_SSM-SSB-17 | 1 | 1
TX_STN22 | CTRL_EQP_BATTERY | 1 | 1
CTRL_EQP_BATTERY | CTRL_EQP | 1 | 1
CTRL_BLDG | CTRL_EQP_BATTERY | 1 | 1
CTRL_BLDG | CTRL_EQP | 1 | 1
CTRL_EQP | CTRL_LINES_JNC1 | 1 | 1
CTRL_EQP | LINE_X02 | 1 | 1
CTRL_EQP | LINE_X03 | 1 | 1
CTRL_EQP | LINE_X05 | 1 | 1
CTRL_EQP | LINE_X08 | 1 | 1
CTRL_LINES_JNC1 | LINE_SSC-17 | 1 | 1
CTRL_LINES_JNC1 | LINE_SSM-SSB-17 | 1 | 1

## supply_setup
input_node | input_capacity | capacity_fraction | commodity_type
LINE_SSC-17 | 100 | 1 | Electric Power

## output_setup
output_node | production_node | output_node_capacity | capacity_fraction | priority
LINE_X02 | BUS_RTX22_SEC-A | 50 | 0.15 | 2
LINE_X03 | BUS_RTX22_SEC-B | 50 | 0.15 | 3
LINE_X05 | BUS_RTX22_SEC-C | 50 | 0.15 | 4
LINE_X08 | BUS_RTX22_SEC-D | 50 | 0.15 | 5
LINE_SSM-SSB-17 | VT_RTX201 | 100 | 0.4 | 1

## comp_type_dmg_algo
id | component_type | damage_state | is_piecewise | damage_function | median | beta | location | damage_ratio | functionality | minimum | upper_limit | lower_limit | recovery_function | recovery_param1 | recovery_param2 | recovery_95percentile | data_source | NOTES
1 | Battery Racks Braced | Minor | no | Lognormal | 0.2 | 0.5 | 0 | 0.1 | 1 | NA | NA | NA | Normal | 1 | 1.2158 | 3 | Fragility source: GA expert judgment.
2 | Battery Racks Braced | Extensive | no | Lognormal | 1.05 | 0.6 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 2 | 1.8237 | 5
3 | Battery Racks Braced | Complete | no | Lognormal | 1.55 | 0.6 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 3 | 2.4316 | 7
4 | Battery Racks Unbraced | Minor | no | Lognormal | 0.15 | 0.5 | 0 | 0.1 | 1 | NA | NA | NA | Normal | 1 | 1.2158 | 3 | Fragility: GA expert judgment.
5 | Battery Racks Unbraced | Extensive | no | Lognormal | 0.6 | 0.6 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 2 | 1.8237 | 5
6 | Battery Racks Unbraced | Complete | no | Lognormal | 1 | 0.6 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 3 | 2.4316 | 7
7 | Building Modern Pre-Cast | Minor | no | Lognormal | 0.55 | 0.36 | 0 | 0.1 | 1 | NA | NA | NA | Normal | 8.75 | 5.3191 | 17.5 | Fragility: GA expert judgment.
8 | Building Modern Pre-Cast | Extensive | no | Lognormal | 0.75 | 0.4 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 17.5 | 10.6383 | 35
9 | Building Modern Pre-Cast | Complete | no | Lognormal | 1.2 | 0.38 | 0 | 1 | 0 | NA | NA | NA | Normal | 26.25 | 18.2371 | 56.25
10 | Building Timber Framed Post War | Minor | no | Lognormal | 0.47 | 0.36 | 0 | 0.1 | 1 | NA | NA | NA | Normal | 8.75 | 5.3191 | 17.5 | Fragility: GA expert judgment.
11 | Building Timber Framed Post War | Extensive | no | Lognormal | 1.27 | 0.4 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 17.5 | 10.6383 | 35
12 | Building Timber Framed Post War | Complete | no | Lognormal | 1.8 | 0.38 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 26.25 | 18.2371 | 56.25
13 | Building Timber Framed Pre War | Minor | no | Lognormal | 0.44 | 0.4 | 0 | 0.1 | 1 | NA | NA | NA | Normal | 8.75 | 5.3191 | 17.5 | Fragility: GA expert judgment.
14 | Building Timber Framed Pre War | Extensive | no | Lognormal | 1.24 | 0.4 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 17.5 | 10.6383 | 35
15 | Building Timber Framed Pre War | Complete | no | Lognormal | 1.7 | 0.4 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 26.25 | 18.2371 | 56.25
16 | Building URM Post War | Minor | no | Lognormal | 0.29 | 0.4 | 0 | 0.1 | 1 | NA | NA | NA | Normal | 8.75 | 5.3191 | 17.5 | Fragility: GA expert judgment.
17 | Building URM Post War | Extensive | no | Lognormal | 0.64 | 0.35 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 17.5 | 10.6383 | 35
18 | Building URM Post War | Complete | no | Lognormal | 1.15 | 0.5 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 26.25 | 18.2371 | 56.25
19 | Building URM Pre War | Minor | no | Lognormal | 0.23 | 0.4 | 0 | 0.1 | 1 | NA | NA | NA | Normal | 8.75 | 5.3191 | 17.5 | Fragility: GA expert judgment.
20 | Building URM Pre War | Extensive | no | Lognormal | 0.52 | 0.3 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 17.5 | 10.6383 | 35
21 | Building URM Pre War | Complete | no | Lognormal | 0.76 | 0.2 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 26.25 | 18.2371 | 56.25
22 | Bus 132 Legacy | Minor | no | Lognormal | 0.1 | 0.45 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
23 | Bus 132 Legacy | Extensive | no | Lognormal | 0.2 | 0.5 | 0 | 0.5 | 0 | NA | NA | NA | Normal | 44 | 41.9453 | 113
24 | Bus 132 Legacy | Complete | no | Lognormal | 0.59 | 0.8 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 75 | 91.1854 | 225
25 | Bus 22 66 132 220 Intermediate | Minor | no | Lognormal | 0.25 | 0.45 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
26 | Bus 22 66 132 220 Intermediate | Extensive | no | Lognormal | 0.35 | 0.5 | 0 | 0.5 | 0 | NA | NA | NA | Normal | 44 | 41.9453 | 113
27 | Bus 22 66 132 220 Intermediate | Complete | no | Lognormal | 0.65 | 0.7 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 75 | 91.1854 | 225
28 | Bus 22 66 132 220 Modern | Minor | no | Lognormal | 0.35 | 0.25 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
29 | Bus 22 66 132 220 Modern | Extensive | no | Lognormal | 0.45 | 0.3 | 0 | 0.5 | 0 | NA | NA | NA | Normal | 44 | 41.9453 | 113
30 | Bus 22 66 132 220 Modern | Complete | no | Lognormal | 0.89 | 0.5 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 75 | 91.1854 | 225
31 | Bus 22 66 Legacy | Minor | no | Lognormal | 0.15 | 0.45 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
32 | Bus 22 66 Legacy | Extensive | no | Lognormal | 0.25 | 0.5 | 0 | 0.5 | 0 | NA | NA | NA | Normal | 44 | 41.9453 | 113
33 | Bus 22 66 Legacy | Complete | no | Lognormal | 0.65 | 0.8 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 75 | 91.1854 | 225
34 | Capacitor Bank 220 132 66 22 All Types Proxy | Minor | no | Lognormal | 0.2 | 0.27 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
35 | Capacitor Bank 220 132 66 22 All Types Proxy | Extensive | no | Lognormal | 101 | 0.5 | 0 | 0.5 | 0 | NA | NA | NA | Normal | 44 | 41.9453 | 113
36 | Capacitor Bank 220 132 66 22 All Types Proxy | Complete | no | Lognormal | 0.37 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 75 | 91.1854 | 225
37 | Circuit Breaker Dead Tank 220kV Intermediate | Slight | no | Lognormal | 0.55 | 0.6 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
38 | Circuit Breaker Dead Tank 220kV Intermediate | Extensive | no | Lognormal | 0.8 | 0.5 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
39 | Circuit Breaker Dead Tank 220kV Intermediate | Complete | no | Lognormal | 1.33 | 0.4 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
40 | Circuit Breaker Dead Tank 66kV 22kV Legacy | Slight | no | Lognormal | 0.5 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
41 | Circuit Breaker Dead Tank 66kV 22kV Legacy | Extensive | no | Lognormal | 0.7 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
42 | Circuit Breaker Dead Tank 66kV 22kV Legacy | Complete | no | Lognormal | 1.53 | 0.4 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
43 | Circuit Breaker Live Tank 132kV Intermediate | Slight | no | Lognormal | 0.3 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
44 | Circuit Breaker Live Tank 132kV Intermediate | Extensive | no | Lognormal | 0.35 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
45 | Circuit Breaker Live Tank 132kV Intermediate | Complete | no | Lognormal | 0.63 | 0.4 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
46 | Circuit Breaker Live Tank 132kV Legacy | Slight | no | Lognormal | 0.15 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
47 | Circuit Breaker Live Tank 132kV Legacy | Extensive | no | Lognormal | 0.2 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
48 | Circuit Breaker Live Tank 132kV Legacy | Complete | no | Lognormal | 0.53 | 0.4 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
49 | Circuit Breaker Live Tank 132kV Modern | Slight | no | Lognormal | 0.43 | 0.3 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
50 | Circuit Breaker Live Tank 132kV Modern | Extensive | no | Lognormal | 0.53 | 0.35 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
51 | Circuit Breaker Live Tank 132kV Modern | Complete | no | Lognormal | 0.68 | 0.35 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
52 | Circuit Breaker Live Tank 220kV Intermediate | Slight | no | Lognormal | 0.25 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
53 | Circuit Breaker Live Tank 220kV Intermediate | Extensive | no | Lognormal | 0.3 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
54 | Circuit Breaker Live Tank 220kV Intermediate | Complete | no | Lognormal | 0.48 | 0.4 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
55 | Circuit Breaker Live Tank 220kV Modern | Slight | no | Lognormal | 0.35 | 0.25 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
56 | Circuit Breaker Live Tank 220kV Modern | Extensive | no | Lognormal | 0.43 | 0.3 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
57 | Circuit Breaker Live Tank 220kV Modern | Complete | no | Lognormal | 0.53 | 0.3 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
58 | Circuit Breaker Live Tank 66kV 22kV Intermediate | Slight | no | Lognormal | 0.3 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
59 | Circuit Breaker Live Tank 66kV 22kV Intermediate | Extensive | no | Lognormal | 0.35 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
60 | Circuit Breaker Live Tank 66kV 22kV Intermediate | Complete | no | Lognormal | 0.78 | 0.4 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
61 | Circuit Breaker Live Tank 66kV 22kV Legacy | Slight | no | Lognormal | 0.2 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
62 | Circuit Breaker Live Tank 66kV 22kV Legacy | Extensive | no | Lognormal | 0.25 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
63 | Circuit Breaker Live Tank 66kV 22kV Legacy | Complete | no | Lognormal | 0.68 | 0.4 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
64 | Circuit Breaker Live Tank 66kV 22kV Modern | Slight | no | Lognormal | 0.58 | 0.4 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
65 | Circuit Breaker Live Tank 66kV 22kV Modern | Extensive | no | Lognormal | 0.68 | 0.4 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
66 | Circuit Breaker Live Tank 66kV 22kV Modern | Complete | no | Lognormal | 0.83 | 0.4 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
67 | Current Transformer 132kV Intermediate | Minor | no | Lognormal | 0.25 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
68 | Current Transformer 132kV Intermediate | Extensive | no | Lognormal | 0.3 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
69 | Current Transformer 132kV Intermediate | Complete | no | Lognormal | 0.48 | 0.27 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
70 | Current Transformer 132kV Legacy | Minor | no | Lognormal | 0.2 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
71 | Current Transformer 132kV Legacy | Extensive | no | Lognormal | 0.3 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
72 | Current Transformer 132kV Legacy | Complete | no | Lognormal | 0.58 | 0.27 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
73 | Current Transformer 132kV Modern | Minor | no | Lognormal | 0.35 | 0.2 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
74 | Current Transformer 132kV Modern | Extensive | no | Lognormal | 0.4 | 0.2 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
75 | Current Transformer 132kV Modern | Complete | no | Lognormal | 0.53 | 0.25 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
76 | Current Transformer 22 66kV Intermediate | Minor | no | Lognormal | 0.3 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
77 | Current Transformer 22 66kV Intermediate | Extensive | no | Lognormal | 0.4 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
78 | Current Transformer 22 66kV Intermediate | Complete | no | Lognormal | 0.63 | 0.27 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
79 | Current Transformer 22 66kV Legacy | Minor | no | Lognormal | 0.2 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
80 | Current Transformer 22 66kV Legacy | Extensive | no | Lognormal | 0.3 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
81 | Current Transformer 22 66kV Legacy | Complete | no | Lognormal | 0.55 | 0.27 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
82 | Current Transformer 220kV Intermediate | Minor | no | Lognormal | 0.25 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
83 | Current Transformer 220kV Intermediate | Extensive | no | Lognormal | 0.3 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
84 | Current Transformer 220kV Intermediate | Complete | no | Lognormal | 0.38 | 0.34 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
85 | Current Transformer 220kV Modern | Minor | no | Lognormal | 0.35 | 0.2 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
86 | Current Transformer 220kV Modern | Extensive | no | Lognormal | 0.38 | 0.2 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
87 | Current Transformer 220kV Modern | Complete | no | Lognormal | 0.43 | 0.2 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
88 | Current Transformer 22 66kV Modern | Minor | no | Lognormal | 0.4 | 0.2 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
89 | Current Transformer 22 66kV Modern | Extensive | no | Lognormal | 0.45 | 0.2 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
90 | Current Transformer 22 66kV Modern | Complete | no | Lognormal | 0.68 | 0.27 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
91 | Disconnection Switches 132kV Intermediate | Slight | no | Lognormal | 0.3 | 0.35 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 9 | 5.4711 | 18 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
92 | Disconnection Switches 132kV Intermediate | Extensive | no | Lognormal | 0.45 | 0.4 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 18 | 10.3343 | 35
93 | Disconnection Switches 132kV Intermediate | Complete | no | Lognormal | 0.67 | 0.35 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 26 | 18.2371 | 56
94 | Disconnection Switches 132kV Legacy | Slight | no | Lognormal | 0.25 | 0.4 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 9 | 5.4711 | 18 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
95 | Disconnection Switches 132kV Legacy | Extensive | no | Lognormal | 0.5 | 0.4 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 18 | 10.3343 | 35
96 | Disconnection Switches 132kV Legacy | Complete | no | Lognormal | 0.7 | 0.35 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 26 | 18.2371 | 56
97 | Disconnection Switches 132kV Modern | Slight | no | Lognormal | 0.45 | 0.3 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 9 | 5.4711 | 18 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
98 | Disconnection Switches 132kV Modern | Extensive | no | Lognormal | 0.6 | 0.35 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 18 | 10.3343 | 35
99 | Disconnection Switches 132kV Modern | Complete | no | Lognormal | 0.77 | 0.35 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 26 | 18.2371 | 56
100 | Disconnection Switches 22 66kV Intermediate | Slight | no | Lognormal | 0.55 | 0.3 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 9 | 5.4711 | 18 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
101 | Disconnection Switches 22 66kV Intermediate | Extensive | no | Lognormal | 0.7 | 0.35 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 18 | 10.3343 | 35
102 | Disconnection Switches 22 66kV Intermediate | Complete | no | Lognormal | 0.87 | 0.35 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 26 | 18.2371 | 56
103 | Disconnection Switches 22 66kV Legacy | Slight | no | Lognormal | 0.3 | 0.4 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 9 | 5.4711 | 18 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
104 | Disconnection Switches 22 66kV Legacy | Extensive | no | Lognormal | 0.55 | 0.4 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 18 | 10.3343 | 35
105 | Disconnection Switches 22 66kV Legacy | Complete | no | Lognormal | 0.75 | 0.35 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 26 | 18.2371 | 56
106 | Disconnection Switches 22 66kV Modern | Slight | no | Lognormal | 0.55 | 0.3 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 9 | 5.4711 | 18 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
107 | Disconnection Switches 22 66kV Modern | Extensive | no | Lognormal | 0.7 | 0.35 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 18 | 10.3343 | 35
108 | Disconnection Switches 22 66kV Modern | Complete | no | Lognormal | 0.97 | 0.35 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 26 | 18.2371 | 56
109 | Disconnection Switches 220kV Intermediate | Slight | no | Lognormal | 0.25 | 0.4 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 9 | 5.4711 | 18 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
110 | Disconnection Switches 220kV Intermediate | Extensive | no | Lognormal | 0.35 | 0.4 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 18 | 10.3343 | 35
111 | Disconnection Switches 220kV Intermediate | Complete | no | Lognormal | 0.47 | 0.35 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 26 | 18.2371 | 56
112 | Disconnection Switches 220kV Modern | Slight | no | Lognormal | 0.45 | 0.3 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 9 | 5.4711 | 18 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
113 | Disconnection Switches 220kV Modern | Extensive | no | Lognormal | 0.5 | 0.32 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 18 | 10.3343 | 35
114 | Disconnection Switches 220kV Modern | Complete | no | Lognormal | 0.57 | 0.35 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 26 | 18.2371 | 56
115 | Lightning Arrestor | Minor | no | Lognormal | 0.2 | 0.35 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 9 | 5.4711 | 18 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
116 | Lightning Arrestor | Extensive | no | Lognormal | 101 | 0.5 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 18 | 10.3343 | 35
117 | Lightning Arrestor | Complete | no | Lognormal | 0.45 | 0.35 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 26 | 18.2371 | 56
118 | Switchgear Low Voltage Legacy | DS1 Minor | no | Lognormal | 0.15 | 0.5 | 0 | 0.3 | 0.5 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
119 | Switchgear Low Voltage Legacy | DS2 Extensive | no | Lognormal | 0.6 | 0.6 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
120 | Switchgear Low Voltage Legacy | DS3 Complete | no | Lognormal | 1 | 0.6 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
121 | Switchgear Low Voltage Intermediate | DS1 Minor | no | Lognormal | 0.2 | 0.5 | 0 | 0.3 | 0.5 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
122 | Switchgear Low Voltage Intermediate | DS2 Extensive | no | Lognormal | 0.8 | 0.6 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
123 | Switchgear Low Voltage Intermediate | DS3 Complete | no | Lognormal | 1.2 | 0.6 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
124 | Switchgear Low Voltage Modern | DS1 Minor | no | Lognormal | 0.25 | 0.5 | 0 | 0.3 | 0.5 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
125 | Switchgear Low Voltage Modern | DS2 Extensive | no | Lognormal | 1 | 0.6 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
126 | Switchgear Low Voltage Modern | DS3 Complete | no | Lognormal | 1.4 | 0.6 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
127 | Transformer 132kV Restrained | Minor | no | Lognormal | 0.28 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
128 | Transformer 132kV Restrained | Minor | no | Lognormal | 0.37 | 0.45 | 0 | 1.2 | 0.5 | NA | NA | NA | Normal | 56 | 102.7356 | 225
129 | Transformer 132kV Restrained | Complete | no | Lognormal | 0.55 | 0.4 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
130 | Transformer 132kV Unestrained | Minor | no | Lognormal | 0.18 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
131 | Transformer 132kV Unestrained | Minor | no | Lognormal | 0.24 | 0.6 | 0 | 1.2 | 0.5 | NA | NA | NA | Normal | 56 | 102.7356 | 225
132 | Transformer 132kV Unestrained | Complete | no | Lognormal | 0.35 | 0.7 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
133 | Transformer 22 66kV Restrained | Minor | no | Lognormal | 0.38 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
134 | Transformer 22 66kV Restrained | Minor | no | Lognormal | 0.47 | 0.45 | 0 | 1.2 | 0.5 | NA | NA | NA | Normal | 56 | 102.7356 | 225
135 | Transformer 22 66kV Restrained | Complete | no | Lognormal | 0.75 | 0.4 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
136 | Transformer 22 66kV Unestrained | Minor | no | Lognormal | 0.2 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
137 | Transformer 22 66kV Unestrained | Minor | no | Lognormal | 0.26 | 0.6 | 0 | 1.2 | 0.5 | NA | NA | NA | Normal | 56 | 102.7356 | 225
138 | Transformer 22 66kV Unestrained | Complete | no | Lognormal | 0.4 | 0.7 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
139 | Transformer 220kV Restrained | Minor | no | Lognormal | 0.225 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
140 | Transformer 220kV Restrained | Minor | no | Lognormal | 0.32 | 0.45 | 0 | 1.2 | 0.5 | NA | NA | NA | Normal | 56 | 102.7356 | 225
141 | Transformer 220kV Restrained | Complete | no | Lognormal | 0.45 | 0.4 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
142 | Transformer 220kV Unestrained | Minor | no | Lognormal | 0.15 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
143 | Transformer 220kV Unestrained | Minor | no | Lognormal | 0.21 | 0.6 | 0 | 1.2 | 0.5 | NA | NA | NA | Normal | 56 | 102.7356 | 225
144 | Transformer 220kV Unestrained | Complete | no | Lognormal | 0.3 | 0.7 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
145 | Voltage Transformer 132kV Intermediate | Minor | no | Lognormal | 0.25 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
146 | Voltage Transformer 132kV Intermediate | Extensive | no | Lognormal | 0.3 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
147 | Voltage Transformer 132kV Intermediate | Complete | no | Lognormal | 0.43 | 0.27 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
148 | Voltage Transformer 132kV Legacy | Minor | no | Lognormal | 0.2 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
149 | Voltage Transformer 132kV Legacy | Extensive | no | Lognormal | 0.3 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
150 | Voltage Transformer 132kV Legacy | Complete | no | Lognormal | 0.5 | 0.27 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
151 | Voltage Transformer 132kV Modern | Minor | no | Lognormal | 0.35 | 0.2 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
152 | Voltage Transformer 132kV Modern | Extensive | no | Lognormal | 0.42 | 0.2 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
153 | Voltage Transformer 132kV Modern | Complete | no | Lognormal | 0.7 | 0.3 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
154 | Voltage Transformer 22 66kV Intermediate | Minor | no | Lognormal | 0.3 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
155 | Voltage Transformer 22 66kV Intermediate | Extensive | no | Lognormal | 0.4 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
156 | Voltage Transformer 22 66kV Intermediate | Complete | no | Lognormal | 0.75 | 0.27 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
157 | Voltage Transformer 22 66kV Legacy | Minor | no | Lognormal | 0.2 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
158 | Voltage Transformer 22 66kV Legacy | Extensive | no | Lognormal | 0.3 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
159 | Voltage Transformer 22 66kV Legacy | Complete | no | Lognormal | 0.65 | 0.27 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
160 | Voltage Transformer 220kV Intermediate | Minor | no | Lognormal | 0.25 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
161 | Voltage Transformer 220kV Intermediate | Extensive | no | Lognormal | 0.32 | 0.45 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
162 | Voltage Transformer 220kV Intermediate | Complete | no | Lognormal | 0.5 | 0.34 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
163 | Voltage Transformer 220kV Modern | Minor | no | Lognormal | 0.35 | 0.2 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
164 | Voltage Transformer 220kV Modern | Extensive | no | Lognormal | 0.4 | 0.2 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
165 | Voltage Transformer 220kV Modern | Complete | no | Lognormal | 0.6 | 0.3 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
166 | Voltage Transformer 22 66kV Modern | Minor | no | Lognormal | 0.4 | 0.2 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
167 | Voltage Transformer 22 66kV Modern | Extensive | no | Lognormal | 0.48 | 0.2 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
168 | Voltage Transformer 22 66kV Modern | Complete | no | Lognormal | 0.85 | 0.35 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
169 | Capacitor Voltage Transformer 330kV | DS1 Minor | no | Lognormal | 0.3 | 0.27 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 3 | 0.6079 | 4 | Fragility source: Assigned the fragility algorithm for: `Current Transformer 330kV`. Recovery source: data provided by network operator for 330kV substations.
170 | Capacitor Voltage Transformer 330kV | DS2 Extensive | no | Lognormal | 0.36 | 0.27 | 0 | 0.2 | 0 | NA | NA | NA | Normal | 225 | 45.5927 | 300
171 | Capacitor Voltage Transformer 330kV | DS3 Complete | no | Lognormal | 0.4 | 0.27 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 225 | 395.1368 | 875
172 | Capacitor Voltage Transformer 220kV | DS1 Minor | no | Lognormal | 0.3 | 0.27 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 3 | 0.6079 | 4 | Fragility source: Assigned the fragility algorithm for: `Current Transformer 330kV`. Recovery source: data provided by network operator for 330kV substations.
173 | Capacitor Voltage Transformer 220kV | DS2 Extensive | no | Lognormal | 0.36 | 0.27 | 0 | 0.2 | 0 | NA | NA | NA | Normal | 225 | 45.5927 | 300
174 | Capacitor Voltage Transformer 220kV | DS3 Complete | no | Lognormal | 0.4 | 0.27 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 225 | 395.1368 | 875
175 | Capacitor Voltage Transformer 66kV | DS1 Minor | no | Lognormal | 0.33 | 0.27 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 18 | 23.1003 | 56 | Fragility source: Assigned the fragility algorithm for: `Current Transformer 330kV`. Recovery source: data provided by network operator for 330kV substations.
176 | Capacitor Voltage Transformer 66kV | DS2 Extensive | no | Lognormal | 0.39 | 0.27 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
177 | Capacitor Voltage Transformer 66kV | DS3 Complete | no | Lognormal | 0.5 | 0.27 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 56 | 102.7356 | 225
178 | Station Transformer 66kV 22kV Restrained | DS1 Minor | no | Lognormal | 0.42 | 0.6 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 7 | 4.2553 | 14
179 | Station Transformer 66kV 22kV Restrained | DS2 Extensive | no | Lognormal | 0.53 | 0.4 | 0 | 1.2 | 0.5 | NA | NA | NA | Normal | 14 | 8.5106 | 28
180 | Station Transformer 66kV 22kV Restrained | DS3 Complete | no | Lognormal | 0.65 | 0.3 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 21 | 14.5897 | 45
181 | Station Transformer 66kV 22kV Unrestrained | DS1 Minor | no | Lognormal | 0.24 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 7 | 4.2553 | 14
182 | Station Transformer 66kV 22kV Unrestrained | DS2 Extensive | no | Lognormal | 0.3 | 0.4 | 0 | 1.2 | 0.5 | NA | NA | NA | Normal | 14 | 8.5106 | 28
183 | Station Transformer 66kV 22kV Unrestrained | DS3 Complete | no | Lognormal | 0.48 | 0.3 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 21 | 14.5897 | 45
184 | Station Transformer 132kV Restrained | DS1 Minor | no | Lognormal | 0.42 | 0.6 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 7 | 4.2553 | 14
185 | Station Transformer 132kV Restrained | DS2 Extensive | no | Lognormal | 0.53 | 0.4 | 0 | 1.2 | 0.5 | NA | NA | NA | Normal | 14 | 8.5106 | 28
186 | Station Transformer 132kV Restrained | DS3 Complete | no | Lognormal | 0.65 | 0.3 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 21 | 14.5897 | 45
187 | Station Transformer 132kV Unrestrained | DS1 Minor | no | Lognormal | 0.24 | 0.5 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 7 | 4.2553 | 14
188 | Station Transformer 132kV Unrestrained | DS2 Extensive | no | Lognormal | 0.3 | 0.4 | 0 | 1.2 | 0.5 | NA | NA | NA | Normal | 14 | 8.5106 | 28
189 | Station Transformer 132kV Unrestrained | DS3 Complete | no | Lognormal | 0.48 | 0.3 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 21 | 14.5897 | 45
190 | Earthing Switch | Minor | no | Lognormal | 0.2 | 0.35 | 0 | 0.01 | 1 | NA | NA | NA | Normal | 9 | 5.4711 | 18 | Fragility source: GA expert judgment. Recovery source: data based on info collated for 132kV substations.
191 | Earthing Switch | Extensive | no | Lognormal | 101 | 0.5 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 18 | 10.3343 | 35
192 | Earthing Switch | Complete | no | Lognormal | 0.45 | 0.35 | 0 | 1.2 | 0 | NA | NA | NA | Normal | 26 | 18.2371 | 56
193 | JUNCTION_NODE | DS1 Minor | no | Lognormal | 10 | 0.5 | 0 | 0.1 | 1 | NA | NA | NA | Normal | 0.1 | 6.0182 | 10 | Uncosted component. Assumed invulnerable in the modelling context.
194 | JUNCTION_NODE | DS2 Extensive | no | Lognormal | 10 | 0.5 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 0.1 | 6.0182 | 10 | Uncosted component. Assumed invulnerable in the modelling context.
195 | JUNCTION_NODE | DS3 Complete | no | Lognormal | 10 | 0.5 | 0 | 1 | 0 | NA | NA | NA | Normal | 0.1 | 6.0182 | 10 | Uncosted component. Assumed invulnerable in the modelling context.
196 | SYSTEM_INPUT | DS1 Minor | no | Lognormal | 10 | 0.5 | 0 | 0.1 | 1 | NA | NA | NA | Normal | 0.1 | 6.0182 | 10 | Uncosted component. Assumed invulnerable in the modelling context.
197 | SYSTEM_INPUT | DS2 Extensive | no | Lognormal | 10 | 0.5 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 0.1 | 6.0182 | 10 | Uncosted component. Assumed invulnerable in the modelling context.
198 | SYSTEM_INPUT | DS3 Complete | no | Lognormal | 10 | 0.5 | 0 | 1 | 0 | NA | NA | NA | Normal | 0.1 | 6.0182 | 10 | Uncosted component. Assumed invulnerable in the modelling context.
199 | SYSTEM_OUTPUT | DS1 Minor | no | Lognormal | 10 | 0.5 | 0 | 0.1 | 1 | NA | NA | NA | Normal | 0.1 | 6.0182 | 10 | Uncosted component. Assumed invulnerable in the modelling context.
200 | SYSTEM_OUTPUT | DS2 Extensive | no | Lognormal | 10 | 0.5 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 0.1 | 6.0182 | 10 | Uncosted component. Assumed invulnerable in the modelling context.
201 | SYSTEM_OUTPUT | DS3 Complete | no | Lognormal | 10 | 0.5 | 0 | 1 | 0 | NA | NA | NA | Normal | 0.1 | 6.0182 | 10 | Uncosted component. Assumed invulnerable in the modelling context.
202 | Generation Plant Liquid Fuel | DS1 Minor | no | Lognormal | 0.1 | 0.5 | 0 | 0.1 | 0.9 | NA | NA | NA | Normal | 0.5 | 0.1 | NA | Fragility: Hazus Earthquake Model Technical Manual v4-2, Table 8-31. Restoration: Hazus Earthquake Model Technical Manual v4-2, Table 8-27.
203 | Generation Plant Liquid Fuel | DS2 Extensive | no | Lognormal | 0.295 | 0.5 | 0 | 0.5 | 0.5 | NA | NA | NA | Normal | 12.8 | 14.1 | NA | Fragility: Hazus Earthquake Model Technical Manual v4-2, Table 8-31. Restoration: Hazus Earthquake Model Technical Manual v4-2, Table 8-27.
204 | Generation Plant Liquid Fuel | DS3 Complete | no | Lognormal | 0.58 | 0.55 | 0 | 1 | 0 | NA | NA | NA | Normal | 65 | 30 | NA | Fragility: Hazus Earthquake Model Technical Manual v4-2, Table 8-31. Restoration: Hazus Earthquake Model Technical Manual v4-2, Table 8-27.

## facility_types
Facility Types | Synonyms | Note
Terminal Substation 220kV MIXED VINTAGE
Terminal Substation 220kV MODERN
Transmission Substation 66kV REGIONAL SML
Transmission Substation 66kV REGIONAL MED
Transmission Substation 66kV REGIONAL LRG
Transmission Substation 66kV METRO SML
Transmission Substation 66kV METRO MED
Transmission Substation 66kV METRO LRG
Generation Plant Liquid Fuel
Generation Plant Gas
Generation Plant Coal
Generation Plant Wind Farm
Generation Plant Solar Farm
JUNCTION_NODE
SYSTEM_INPUT
SYSTEM_OUTPUT

## asset_names
Component Types | Synonyms | Note
Battery Racks Braced
Battery Racks Unbraced
Building Modern Pre-Cast
Building Timber Framed Post War
Building Timber Framed Pre War
Building URM Post War
Building URM Pre War
Bus 132 Legacy
Bus 22 66 132 220 Intermediate
Bus 22 66 132 220 Modern
Bus 22 66 Legacy
Capacitor Bank 220 132 66 22 All Types Proxy
Capacitor Voltage Transformer 220kV
Capacitor Voltage Transformer 330kV
Capacitor Voltage Transformer 66kV
Circuit Breaker Dead Tank 220kV Intermediate
Circuit Breaker Dead Tank 66kV 22kV Legacy
Circuit Breaker Live Tank 132kV Intermediate
Circuit Breaker Live Tank 132kV Legacy
Circuit Breaker Live Tank 132kV Modern
Circuit Breaker Live Tank 220kV Intermediate
Circuit Breaker Live Tank 220kV Modern
Circuit Breaker Live Tank 66kV 22kV Intermediate
Circuit Breaker Live Tank 66kV 22kV Legacy
Circuit Breaker Live Tank 66kV 22kV Modern
Current Transformer 132kV Intermediate
Current Transformer 132kV Legacy
Current Transformer 132kV Modern
Current Transformer 22 66kV Intermediate
Current Transformer 22 66kV Legacy
Current Transformer 22 66kV Modern
Current Transformer 220kV Intermediate
Current Transformer 220kV Modern
Disconnection Switches 132kV Intermediateiate
Disconnection Switches 132kV Legacy
Disconnection Switches 132kV Modern
Disconnection Switches 22 66kV Intermediate
Disconnection Switches 22 66kV Legacy
Disconnection Switches 22 66kV Modern
Disconnection Switches 220kV Intermediate
Disconnection Switches 220kV Modern
Generation Plant Liquid Fuel
JUNCTION_NODE
Lightning Arrestor
Station Transformer 132kV Restrained
Station Transformer 132kV Unrestrained
Station Transformer 66kV 22kV Restrained
Station Transformer 66kV 22kV Unrestrained
Switchgear Low Voltage Intermediate
Switchgear Low Voltage Legacy
Switchgear Low Voltage Modern
SYSTEM_INPUT
SYSTEM_OUTPUT
Terminal Substation 220kV MIXED VINTAGE
Terminal Substation 220kV MODERN
Transformer 132kV Restrained
Transformer 132kV Unestrained
Transformer 22 66kV Restrained
Transformer 22 66kV Unestrained
Transformer 220kV Restrained
Transformer 220kV Unestrained
Transmission Substation 66kV REGIONAL LRG
Transmission Substation 66kV REGIONAL MED
Transmission Substation 66kV REGIONAL SML
Voltage Transformer 132kV Intermediate
Voltage Transformer 132kV Legacy
Voltage Transformer 132kV Modern
Voltage Transformer 22 66kV Intermediate
Voltage Transformer 22 66kV Legacy
Voltage Transformer 22 66kV Modern
Voltage Transformer 220kV Intermediate
Voltage Transformer 220kV Modern

## damage_state_def
component_type | damage_state | damage_state_definition
Battery Racks Braced | DS1 Minor | Sliding of support frame with some displacement of batteries but still retained on rack.
| DS2 Extensive | Yielding of the frame and braces with lateral displacement of the rack. Many batteries have fallen out.
| DS3 Complete | Complete collapse of rack.
Battery Racks Unbraced | DS1 Minor | Sliding of support frame with some displacement of batteries but still retained on rack.
| DS2 Extensive | Yielding of the frame and braces with lateral displacement of the rack. Many batteries have fallen out.
| DS3 Complete | Yielding of the frame with lateral displacement of the rack. Many batteries have fallen out.
Building Modern Pre-Cast | DS1 Minor | Minor diagonal hairline cracking to panels at door corners or other openings. Hairline cracks around metal connectors between wall panels or at ceiling to wall interface. Some minor separation of silicone sealant in vertical panel joints.
| DS2 Extensive | Wider cracks in proximity to doors and other openings. Some failures of wall to wall welded metal connectors with peripheral panel damage. Lateral displacement of some panels and significant distress between roof diaphragm and top of walls. Vertical cracking mid-span at top of long span walls indicating "chord" yielding.
| DS3 Complete | Structure has collapsed or in imminent danger of doing so. Separation or top of wall from roof diaphragm with lateral displacment of top of wall with partial loss of roof support. Many wall to wall welded metal connectors have failed. Some foundation settlement and in-plane rotation of short walls with distress at interface between precast wall and floor.
Building Timber Framed Post War | DS1 Minor | Minor damage to non-structural linings at door or window openings and wall to ceiling intersections. Minor lateral displacement of structure on foundations.
| DS2 Extensive | Signiciant damage to internal and external linings with larger cracks at the corners of doors, windows and other openeings. Significant lining damage between ceilings and internal walls. Permanent in plane racking displacment to walls and out of plane due the loads applied by internal equipment. Major lateral movement between superstructure and foundations.
| DS3 Complete | Structure has large lateral displacements with racking of walls and roof may have partially collapsed. Building has translated off foundations with resultant uneven settlement.
Building Timber Framed Pre War | DS1 Minor | Minor damage to non-structural linings at door or window openings and wall to ceiling intersections. Minor lateral displacement of structure on foundations.
| DS2 Extensive | Signiciant damage to internal and external linings with larger cracks at the corners of doors, windows and other openeings. Significant lining damage between ceilings and internal walls. Permanent in plane racking displacment to walls and out of plane due the loads applied by internal equipment. Major lateral movement between superstructure and foundations.
| DS3 Complete | Structure has large lateral displacements with racking of walls and roof may have partially collapsed. Building has translated off foundations with resultant uneven settlement.
Building URM Post War | DS1 Minor | Minor hairline diagonal cracking of walls. Wider cracking present at corners of doors and windows. Minor lateral displacment of roof structure leading to non-structural damage to linings at ceiling/wall interface.
| DS2 Extensive | Most walls exhibit diagonal cracking with some walls having wide cracks, particularly adjacent to door, windows and other openings. Some walls exhibit permanent out of plane offsets with lack of alignment across cracks or adjacent to doors. Signficant movement between roof structure and walls. Some separation evident between suspended floor and exterior walls. Where present, parapets and gables may be offset or have fallen.
| DS3 Complete | Structure may have collapsed or be in imminent danger of doing so. Relative movement of roof structure to supporting walls has caused partial collapse of roof structure into the buliding. Suspended floor unseating in locations, particularly where the rocking of unbraced equipment has transfered large forces into the floor structure dislodged the floor. Foundation settlement and spreading may add to the overall damage.
Building URM Pre War | DS1 Minor | Minor hairline diagonal cracking of walls. Wider cracking present at corners of doors and windows. Minor lateral displacment of roof structure leading to non-structural damage to linings at ceiling/wall interface.
| DS2 Extensive | Most walls exhibit diagonal cracking with some walls having wide cracks, particularly adjacent to door, windows and other openings. Some walls exhibit permanent out of plane offsets with lack of alignment across cracks or adjacent to doors. Signficant movement between roof structure and walls. Some separation evident between suspended floor and exterior walls. Where present, parapets and gables may be offset or have fallen.
| DS3 Complete | Structure may have collapsed or be in imminent danger of doing so. Relative movement of roof structure to supporting walls has caused partial collapse of roof structure into the buliding. Suspended floor unseating in locations, particularly where the rocking of unbraced equipment has transfered large forces into the floor structure dislodged the floor. Foundation settlement and spreading may add to the overall damage.
Bus 22 66 Legacy | DS1 Minor | Minor yielding or cracking of base structure or hold-down of pole insulators.
| DS2 Extensive | Permanent displacement of bus due to yielding of pole insulators. Some failures of bus conductors due to connection failures with dropping of bus elements.
| DS3 Complete | Major drift or collapse in supporting structure or insulator.
Bus 132 Legacy | DS1 Minor | Minor yielding or cracking of base structure or hold-down of pole insulators.
| DS2 Extensive | Permanent displacement of bus due to yielding of pole insulators. Some failures of bus conductors due to connection failures with dropping of bus elements.
| DS3 Complete | Major drift or collapse in supporting structure or insulator.
Bus 22 66 132 220 Intermediate | DS1 Minor | Minor yielding or cracking of base structure or hold-down of pole insulators.
| DS2 Extensive | Permanent displacement of bus due to yielding of pole insulators. Some failures of bus conductors due to connection failures with dropping of bus elements.
| DS3 Complete | Major drift or collapse in supporting structure or insulator.
Bus 22 66 132 220 Modern | DS1 Minor | Minor yielding or cracking of base structure or hold-down of pole insulators.
| DS2 Extensive | Permanent displacement of bus due to yielding of pole insulators. Some failures of bus conductors due to connection failures with dropping of bus elements.
| DS3 Complete | Major drift or collapse in supporting structure or insulator.
Capacitor Bank 220 132 66 22 All Types Proxy | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramic insulation and permanent drift, with foundation rotations.
| DS3 Complete | Overturning or collapse due to failure of ceramic insulators.
Capacitor Voltage Transformer 220kV | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking.
| DS3 Complete | Overturning.
Capacitor Voltage Transformer 330kV | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking.
| DS3 Complete | Overturning.
Capacitor Voltage Transformer 66kV | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking.
| DS3 Complete | Overturning.
Circuit Breaker Dead Tank 220kV Intermediate | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of interrupter casing. Interrupter head falling off in some instances. In other instances damage to conductor connections.
| DS3 Complete | Overturning.
Circuit Breaker Dead Tank 66kV 22kV Legacy | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of interrupter casing. Interrupter head falling off in some instances. In other instances damage to conductor connections.
| DS3 Complete | Overturning.
Circuit Breaker Live Tank 132kV Legacy | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of interrupter casing. Interrupter head falling off in some instances. In other instances damage to conductor connections.
| DS3 Complete | Overturning.
Circuit Breaker Live Tank 132kV Intermediate | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of interrupter casing. Interrupter head falling off in some instances. In other instances damage to conductor connections.
| DS3 Complete | Overturning.
Circuit Breaker Live Tank 132kV Modern | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of interrupter casing. Interrupter head falling off in some instances. In other instances damage to conductor connections.
| DS3 Complete | Overturning.
Circuit Breaker Live Tank 220kV Legacy | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of interrupter casing. Interrupter head falling off in some instances. In other instances damage to conductor connections.
| DS3 Complete | Overturning.
Circuit Breaker Live Tank 220kV Intermediate | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of interrupter casing. Interrupter head falling off in some instances. In other instances damage to conductor connections.
| DS3 Complete | Overturning.
Circuit Breaker Live Tank 220kV Modern | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of interrupter casing. Interrupter head falling off in some instances. In other instances damage to conductor connections.
| DS3 Complete | Overturning.
Circuit Breaker Live Tank 66kV 22kV Legacy | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of interrupter casing. Interrupter head falling off in some instances. In other instances damage to conductor connections.
| DS3 Complete | Overturning.
Circuit Breaker Live Tank 66kV 22kV Intermediate | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of interrupter casing. Interrupter head falling off in some instances. In other instances damage to conductor connections.
| DS3 Complete | Overturning.
Circuit Breaker Live Tank 66kV 22kV Modern | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of interrupter casing. Interrupter head falling off in some instances. In other instances damage to conductor connections.
| DS3 Complete | Overturning.
Current Transformer 132kV Legacy | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Current Transformer 132kV Intermediate | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Current Transformer 132kV Modern | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Current Transformer 22 66kV Legacy | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Current Transformer 22 66kV Intermediate | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Current Transformer 22 66kV Modern | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Current Transformer 220kV Legacy | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Current Transformer 220kV Intermediate | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Current Transformer 220kV Modern | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Disconnection Switches 132kV Legacy | DS1 Minor | Misalignment of disconnection switches. Cracking and yielding of concrete support structure.
| DS2 Extensive | Major horizontal displacement of support structure.
| DS3 Complete | Collapse of disconnection switch, or support structure.
Disconnection Switches 132kV Intermediate | DS1 Minor | Misalignment of disconnection switches. Cracking and yielding of concrete support structure.
| DS2 Extensive | Major horizontal displacement of support structure.
| DS3 Complete | Collapse of disconnection switch, or support structure.
Disconnection Switches 132kV Modern | DS1 Minor | Misalignment of disconnection switches. Cracking and yielding of concrete support structure.
| DS2 Extensive | Major horizontal displacement of support structure.
| DS3 Complete | Collapse of disconnection switch, or support structure.
Disconnection Switches 22 66kV Legacy | DS1 Minor | Misalignment of disconnection switches. Cracking and yielding of concrete support structure.
| DS2 Extensive | Major horizontal displacement of support structure.
| DS3 Complete | Collapse of disconnection switch, or support structure.
Disconnection Switches 22 66kV Intermediate | DS1 Minor | Misalignment of disconnection switches. Cracking and yielding of concrete support structure.
| DS2 Extensive | Major horizontal displacement of support structure.
| DS3 Complete | Collapse of disconnection switch, or support structure.
Disconnection Switches 22 66kV Modern | DS1 Minor | Misalignment of disconnection switches. Cracking and yielding of concrete support structure.
| DS2 Extensive | Major horizontal displacement of support structure.
| DS3 Complete | Collapse of disconnection switch, or support structure.
Disconnection Switches 220kV Legacy | DS1 Minor | Misalignment of disconnection switches. Cracking and yielding of concrete support structure.
| DS2 Extensive | Major horizontal displacement of support structure.
| DS3 Complete | Collapse of disconnection switch, or support structure.
Disconnection Switches 220kV Intermediate | DS1 Minor | Misalignment of disconnection switches. Cracking and yielding of concrete support structure.
| DS2 Extensive | Major horizontal displacement of support structure.
| DS3 Complete | Collapse of disconnection switch, or support structure.
Disconnection Switches 220kV Modern | DS1 Minor | Misalignment of disconnection switches. Cracking and yielding of concrete support structure.
| DS2 Extensive | Major horizontal displacement of support structure.
| DS3 Complete | Collapse of disconnection switch, or support structure.
Earthing Switch | DS1 Minor | x
| DS2 Extensive | x
| DS3 Complete | x
Lightning Arrestor | DS1 Minor | Damage to support stucture.
| DS2 Extensive | Minor permanent horizontal drift.
| DS3 Complete | Collapse due to failure of base fixing or supporting structure.
Station Transformer 132kV Restrained | DS1 Minor | Damage to support stucture.
| DS2 Extensive | Minor permanent horizontal drift.
| DS3 Complete | Collapse due to failure of base fixing or supporting structure.
Station Transformer 132kV Unrestrained | DS1 Minor | Damage to support stucture.
| DS2 Extensive | Minor permanent horizontal drift.
| DS3 Complete | Collapse due to failure of base fixing or supporting structure.
Station Transformer 66kV 22kV Restrained | DS1 Minor | Damage to support stucture.
| DS2 Extensive | Minor permanent horizontal drift.
| DS3 Complete | Collapse due to failure of base fixing or supporting structure.
Station Transformer 66kV 22kV Unrestrained | DS1 Minor | Damage to support stucture.
| DS2 Extensive | Minor permanent horizontal drift.
| DS3 Complete | Collapse due to failure of base fixing or supporting structure.
Switchgear Low Voltage Legacy | DS1 Minor | Partial overturning without equipment damage in panel.
| DS2 Extensive | Partial overturning with equipment damage.
| DS3 Complete | Overturning.
Switchgear Low Voltage Intermediate | DS1 Minor | Partial overturning without equipment damage in panel.
| DS2 Extensive | Partial overturning with equipment damage.
| DS3 Complete | Overturning.
Switchgear Low Voltage Modern | DS1 Minor | Partial overturning without equipment damage in panel.
| DS2 Extensive | Partial overturning with equipment damage.
| DS3 Complete | Overturning.
Switchgear High Voltage Legacy | DS1 Minor | Partial overturning without equipment damage in panel.
| DS2 Extensive | Partial overturning with equipment damage.
| DS3 Complete | Overturning.
Switchgear High Voltage Intermediate | DS1 Minor | Partial overturning without equipment damage in panel.
| DS2 Extensive | Partial overturning with equipment damage.
| DS3 Complete | Overturning.
Switchgear High Voltage Modern | DS1 Minor | Partial overturning without equipment damage in panel.
| DS2 Extensive | Partial overturning with equipment damage.
| DS3 Complete | Overturning.
Transformer 132kV Restrained | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Transformer 132kV Unestrained | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Transformer 22 66kV Restrained | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Transformer 22 66kV Unestrained | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Transformer 220kV Restrained | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Transformer 220kV Unestrained | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Voltage Transformer 132kV Legacy | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Voltage Transformer 132kV Intermediate | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Voltage Transformer 132kV Modern | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Voltage Transformer 22 66kV Legacy | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Voltage Transformer 22 66kV Intermediate | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Voltage Transformer 22 66kV Modern | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Voltage Transformer 220kV Legacy | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Voltage Transformer 220kV Intermediate | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.
Voltage Transformer 220kV Modern | DS1 Minor | Yielding of holding down bolts and support structure. Minor rotation of foundation.
| DS2 Extensive | Cracking of ceramics with some oil leakage.
| DS3 Complete | Overturning.

## VALIDATION_TABLES
INFRASTRUCTURE_LEVEL | SYSTEM_CLASSES | RESTORATION_TIME_UNIT | COMPONENT_LOCATION_CONF
facility | PowerStation | days | defined
network | Substation | weeks | undefined
| PotableWaterTreatmentPlant | months | schematic
| PWTP | years | geospatial
WasteWaterTreatmentPlant
WWTP
PotableWaterPumpStation
ElectricPowerNetwork
PotableWaterNetwork
RailNetwork

## REFERENCES
References for Earthquake Fragility Data for Electrical Power Network Components
REFERENCES
Anagnos (1999) | Anagnos T (1999) Development of an electrical substation eqyuipment performance database for evaluation of equipment fragilities. Report Department of Civil and Environmental Engineering, San Jose State University, San Jose, USA, for PG&E/PEER
Anagnos and Ostrom (2000) | Anagnos T, Ostrom DK (2000) Electrical substation equipment damage database for updating fragility estimates. In Proceedings of the 12th World Conference on Earthquake Engineering, Auckland, New Zealand
Ang, Pires, and Villaverde (1996) | Ang AH-S, Pires JA, Villaverde R (1996) A model for the seismic reliability assessment of electric power transmission systems. Reliability Engineering & System Safety 51(1): 7-22
Bettinali et al (2004) | Bettinali F, Rasulo A, Vanzi I, Imperatore S, Evangelista S (2004) Influenza dei parametri di sismicità sull’analisi affidabilistica della rete di trasmissione elettrica: applicazione ad un caso studio. In 23° Convegno Nazionale of GNGTS, rome, Italy
NIBS (2009) | National Institute of Building Sciences. (2009). Multi-hazard Loss Estimation Methodology, Earthquake Model, HAZUS-MH 2.1, Technical Manual. Washington, D.C. Retrieved from https://www.fema.gov/media-library-data/20130726-1820-25045-6286/hzmh2_1_eq_tm.pdf
Hwang and Chou (1998) | Hwang HHM, Chou T (1998) Evaluation of seismic performance of an electric substation using event tree/fault tree technique. Probabilistic Engineering Mechanics 13(2):117-124
Hwang and Huo (1998) | Hwang HHM, Huo JR (1998) Seismic fragility analysis of electric substation equipment and structures. Probabilistic Engineering Mechanics 13(2):107-116
Liu, Liu, and Wang (2003) | Liu G-Y, Liu C-W, Wang YJ (2003) Montecarlo simulation for the seismic response analysis of electric power system in Taiwan. In Proceedings of NCREE/JRC joint workshop, Taipei, Taiwan
Rasulo, Goretti, and Nuti (2004) | Rasulo A, Goretti A, Nuti C (2004) Performance of lifelines during the 2002 Molise, Italy, earthquake, Earthquake Spectra 20(S1):S301-S314
Shinozuka, Dong, Chen, and Jin (2007) | Shinozuka M, Dong X, Chen TC, Jin X (2007) Seismic performance of electric transmission network under component failures. Earthquake Engineering and Structural Dynamics 36(2):227-244
Straub and Der Kiureghian (2008) | Straub D, Der Kiureghian A (2008) Improved seismic fragility modeling from empirical data. Structural Safety 30(4):320-336
Vanzi (1996) | Vanzi I (1996) Seismic reliability of electric power networks: methodology and application. Structural Safety 18(4):311-327
Vanzi (2000) | Vanzi I (2000) Structural upgrading strategy for electric power networks under seismic action. Earthquake Engineering and Structural Dynamics 29(7):1053-1073
Vanzi, Rasulo, and Sigismondo (2004) | Vanzi I, Rasulo A, Sigismondo S (2004) Valutazione della sicurezza al sisma del sistema reti elettriche e procedura di adeguamento: Fase B, fragilità dei component. Report Dipartimento di Progettazione, Riabilitazione e Controllo delle Strutture (PRICOS), Università G. D’Annunzio di Chieti, Pescara, Italy for Pricos—Cesi S.p.A., contract U0950

## component_costing
component_id | component_type | value_aud_1k | value_fraction | 132kV substation components | Value (AUD)
BUS_KEL22_PRI-A | Bus 22 66 Legacy | 140 | 0.015748 | Bus 132kV | $2M
BUS_KEL22_PRI-B | Bus 22 66 Legacy | 140 | 0.015748 | Capacitor Bank | $500k
BUS_KEL22_PRI-C | Bus 22 66 Legacy | 140 | 0.015748 | Capacitor Voltage Transformer 132kV | $200k
BUS_KEL22_SEC-A | Bus 22 66 Legacy | 105 | 0.011811 | Circuit Breaker | $200k
BUS_KEL22_SEC-B | Bus 22 66 Legacy | 105 | 0.011811 | Current Transformer 132kV | $200k
BUS_KEL22_SEC-C | Bus 22 66 Legacy | 105 | 0.011811 | Disconnect Switch 132kV | $175k
BUS_KEL22_SEC-D | Bus 22 66 Legacy | 105 | 0.011811 | Earthing Switch | $175k
BUS_KEL66_A | Bus 22 66 Legacy | 340 | 0.038245 | Electrical Control Equipment 132kV | $350k
BUS_KEL66_B | Bus 22 66 Legacy | 330 | 0.03712 | Lighting Arrester 132kV | $150k
BUS_KEL66_C | Bus 22 66 Legacy | 340 | 0.038245 | Power Transformer 19/33.3 MVA | $2M
CB_KEL502_0 | Circuit Breaker Live Tank 66kV 22kV Legacy | 70 | 0.007874 | Power Transformer 20/33 MVA | $2.5M
CB_KEL503_0 | Circuit Breaker Live Tank 66kV 22kV Legacy | 70 | 0.007874 | Power Transformer 24/33.3 MVA | $3M
CB_KEL505_0 | Circuit Breaker Live Tank 66kV 22kV Legacy | 70 | 0.007874 | Voltage Transformer 132kV | $200k
CB_KEL508_0 | Circuit Breaker Live Tank 66kV 22kV Legacy | 70 | 0.007874 | Control Building | $350k
CB_KEL701_0 | Circuit Breaker Live Tank 66kV 22kV Intermediate | 100 | 0.011249
CB_KEL706_0 | Circuit Breaker Live Tank 66kV 22kV Intermediate | 100 | 0.011249
CT_KEL502 | Current Transformer 66kV 22kV Legacy | 70 | 0.007874 | Component values used | Value (1k AUD)
CT_KEL503 | Current Transformer 66kV 22kV Legacy | 70 | 0.007874 | Battery Backup System | 50
CT_KEL505 | Current Transformer 66kV 22kV Legacy | 70 | 0.007874 | Building Modern Precast | 350
CT_KEL508 | Current Transformer 66kV 22kV Legacy | 70 | 0.007874 | Bus 22 Legacy | 400
CTRL_BLDG | Building Timber Framed Pre War | 250 | 0.028121 | Bus 66 Intermediate | 1000
CTRL_EQP | Control Equipment Electro Mech | 300 | 0.033746 | Bus 132 Intermediate | 2000
CTRL_EQP_BATTERY | Battery Backup System | 50 | 0.0056243 | Circuit Breaker Live Tank 132kV Intermediate | 100
DS_KEL502_4 | Disconnect Switch 66kV 22kV Legacy | 60 | 0.0067492 | Circuit Breaker Live Tank 66kV 22kV Intermediate | 100
DS_KEL502_5 | Disconnect Switch 66kV 22kV Legacy | 60 | 0.0067492 | Circuit Breaker Live Tank 66kV 22kV Legacy | 70
DS_KEL503_4 | Disconnect Switch 66kV 22kV Legacy | 60 | 0.0067492 | Control Equipment Solid State | 350
DS_KEL503_5 | Disconnect Switch 66kV 22kV Legacy | 60 | 0.0067492 | Current Transformer 132kV Intermediate | 100
DS_KEL503_8 | Disconnect Switch 66kV 22kV Legacy | 60 | 0.0067492 | Current Transformer 66kV 22kV Intermediate | 100
DS_KEL504_4 | Disconnect Switch 66kV 22kV Legacy | 60 | 0.0067492 | Current Transformer 66kV 22kV Legacy | 70
DS_KEL505_4 | Disconnect Switch 66kV 22kV Legacy | 60 | 0.0067492 | Disconnect Switch 132kV Intermediate | 175
DS_KEL505_5 | Disconnect Switch 66kV 22kV Legacy | 60 | 0.0067492 | Disconnect Switch 66kV 22kV Intermediate | 90
DS_KEL505_8 | Disconnect Switch 66kV 22kV Legacy | 60 | 0.0067492 | Disconnect Switch 66kV 22kV Legacy | 60
DS_KEL506_4 | Disconnect Switch 66kV 22kV Legacy | 60 | 0.0067492 | Lightning Arrester General | 70
DS_KEL508_4 | Disconnect Switch 66kV 22kV Legacy | 60 | 0.0067492 | Power Transformer 132kV Restrained Intermediate | 3000
DS_KEL508_5 | Disconnect Switch 66kV 22kV Legacy | 60 | 0.0067492 | Power Transformer 66kV 22kV Restrained | 1500
DS_KEL508_8 | Disconnect Switch 66kV 22kV Legacy | 60 | 0.0067492 | Station Transformer 66kV 22kV Restrained | 600
DS_KEL509_4 | Disconnect Switch 66kV 22kV Legacy | 60 | 0.0067492 | Voltage Transformer 132kV Intermediate | 200
DS_KEL510_4 | Disconnect Switch 66kV 22kV Legacy | 60 | 0.0067492 | Voltage Transformer 66kV 22kV Intermediate | 80
DS_KEL701_4 | Disconnect Switch 66kV 22kV Intermediate | 90 | 0.010124 | JUNCTION_NODE | 0
DS_KEL701_5 | Disconnect Switch 66kV 22kV Intermediate | 90 | 0.010124 | SYSTEM_INPUT | 0
DS_KEL702_4 | Disconnect Switch 66kV 22kV Intermediate | 90 | 0.010124 | SYSTEM_OUTPUT | 0
DS_KEL703_4 | Disconnect Switch 66kV 22kV Intermediate | 90 | 0.010124
DS_KEL705_4 | Disconnect Switch 66kV 22kV Intermediate | 90 | 0.010124
DS_KEL706_4 | Disconnect Switch 66kV 22kV Intermediate | 90 | 0.010124
DS_KEL706_5 | Disconnect Switch 66kV 22kV Intermediate | 90 | 0.010124
DS_KEL707_4 | Disconnect Switch 66kV 22kV Intermediate | 90 | 0.010124
JNC_CTRL_PWR1 | JUNCTION_NODE | 0 | 0
JNC_CTRL_LINES_A | JUNCTION_NODE | 0 | 0
LA_KEL702 | Lightning Arrester General | 70 | 0.007874
LA_KEL707 | Lightning Arrester General | 70 | 0.007874
LINE_502 | SYSTEM_OUTPUT | 0 | 0
LINE_503 | SYSTEM_OUTPUT | 0 | 0
LINE_505 | SYSTEM_OUTPUT | 0 | 0
LINE_508 | SYSTEM_OUTPUT | 0 | 0
LINE_CUN71 | SYSTEM_INPUT | 0 | 0
LINE_MER-BDE71 | SYSTEM_OUTPUT | 0 | 0
PTX_66-22KV_T1 | Power Transformer 66kV 22kV Unrestrained | 1500 | 0.16873
PTX_66-22KV_T3 | Power Transformer 66kV 22kV Unrestrained | 1500 | 0.16873
TX_STN22 | Station Transformer 66kV 22kV Restrained | 600 | 0.067492
VT_KEL504 | Voltage Transformer 66kV 22kV Legacy | 80 | 0.0089989
VT_KEL510 | Voltage Transformer 66kV 22kV Legacy | 80 | 0.0089989
VT_KEL701 | Voltage Transformer 66kV 22kV Intermediate | 80 | 0.0089989
VT_KEL706 | Voltage Transformer 66kV 22kV Intermediate | 80 | 0.0089989
|  | 8890 | 1